{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["BinResultsHPEFT1Y","Plot","Plot (2)","Plot3","Plot4","Plot5"],"not_rendered":{"charts":44,"images":0,"macros":1,"external_links":0,"defined_names":0,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"BinResultsHPEFT1Y","index":0,"n_rows":44,"n_cols":70,"rows_kept":44,"cut":false,"hidden":false,"merged":[]}
[]
["HP EFT / BH ExFT (°C)","Count","ODA Temperature (°C)","EL 007 (kW)","GHE EFT (°C)","GHE ExFT (°C)","Clg Provided (kW)","Bldg Htg Provided (kW)","EL 003 (kW)","CP Energy (kW)","DHW Provided by HP (kW)","DHW by LPS (kW)","Useful Bldg Htg by LPS (kW)","Bldg Htg Uncertainty (kW)","Bldg Clg Uncertainty (kW)","DHW Htg by HP Uncertainty (kW)","Bldg + DHW Htg by HP Uncertainty (kW)","EL007+EL011 Uncertainty (kW)","EL011 Uncertainty (kW)","LPS DHW Uncertainty (kW)","CP Power for Heat Extraction from GHE (kW)","CP Power for Heat Rejection to GHE (kW)","Heat Extraction by GHE (kW)","Heat Rejection to GHE (kW)","EL007 Uncertainty (kW)","LPS Electricity going to bldg heat (kW)","Alt Calc GHE Heat Extraction (kW)","Alt Calc GHE Heat Extraction (kW)","HtgFrac","COP H4","COP H3","COP H2","COP C3","COP C2","Overall (H+C) COP","Not used","Not used","Not used","Not used","Error COP H4","Error COP H3","Error COP H2","Error COP H3b","Error COP C2","BPF0, heating","BPF0, cooling","BPF1*, heating","BPF2, heating","BPF3+, heating","BPF4+, heating","BPF2, cooling","BPF3, cooling","BPF4, cooling","Error BPF0, heating","Error BPF0, cooling","Error BPF1*, heating","Error BPF2, heating","Error BPF3+, heating","Error BPF4+, heating","Error BPF2, cooling","Error BPF3, cooling","Error BPF4, cooling","Htg & Clg Provided Boundary 2","Htg & Clg Provided Boundary 4+","Electricity Used Boundary 2","Electricity Used Boundary 4+","BPFHC2","BPFHC4+","Error BPFHC2","Error BPFHC4+"]
[3,2,7.9499444521628249,3.5188290633289467,11.417540168328188,3.1339850249538559,0,0,8.9706886849089216,0,1.8947127785524307,0.2046235737962967,0,0,0,0.14531818640295352,0.14531818640295352,0.19337051826053631,0.19,5.8773646931566184E-2,0,0,0,0,3.5188290633289473E-2,2.7953764262037035,1.375883715223484,0,1,0.16808786333202658,0.59660083356327487,3.6519017774282809,0,0,0.59660083356327487,0,0,0,0,1.1922703489092594E-2,5.2728816308009463E-2,1.518394834290101,5.5310988198773559E-2,0,0,0,3.6519017774282809,3.6519017774282809,0.59660083356327487,0.16808786333202658,0,0,0,0,0,1.5141632054743852,1.518394834290101,5.2728816308009463E-2,1.1922703489092594E-2,0,0,0,1.8947127785524307,2.0993363523487272,0.51882906332894674,12.489517748237869,3.6519017774282809,0.16808786333202658,0.63391163531794925,0.43749102886998698]
[4,1,8.1,2.7307073424787487,17.11909394108671,3.7610169489606995,0,0,7.4028826839064372,0,1.5988462543792068,0.17267083339768741,0,0,0,0.12262620522412453,0.12262620522412453,0.19195227599334877,0.19,4.9595920984147307E-2,0,0,0,0,2.7307073424787488E-2,2.7307073424787487,1.7715170877768942,0,1,0.17481633687215811,0.64873926993906006,0,0,0,0.64873926993906006,0,0,0,0,1.25458641922163E-2,6.4001315103745349E-2,0,6.6528470672524515E-2,0,0,0,0,0,0.64873926993906006,0.17481633687215811,0,0,0,0,0,0,0,6.4001315103745349E-2,1.25458641922163E-2,0,0,0,1.5988462543792068,1.7715170877768942,-0.17267083339768741,10.133590026385185,0,0.17481633687215811,0,0]
[4.5,1,7.8,3.1990883824346859,-0.70075041712599073,4.6563368541610197,0,0,8.9930558740221986,4.0036248068627855E-7,1.09730093713965,0.11850537022243837,0,0,0,8.4159342739653503E-2,8.4159342739653503E-2,0.19267437984294347,0.19,3.403807615969897E-2,4.0036248068627855E-7,0,1.2456346052757565,0,3.1990883824346859E-2,2.8814946297775617,0.89821215434248347,0,1,9.9720466046668108E-2,0.38004769167394964,5.511616082647862,0,0,0.38004769167394964,0,0,0,0,7.0803555264690766E-3,3.4871208961912509E-2,5.7041102100577019,3.6458322706675282E-2,0,3111267.0776256574,0,5.5116271663899692,5.511616082647862,0.38004769167394964,9.9720466046668108E-2,0,0,0,0,0,5.701570270272696,5.7041102100577019,3.4871208961912509E-2,7.0803555264690766E-3,0,0,0,1.09730093713965,1.2158063073620884,0.19908878279716655,12.192144256456885,5.511616082647862,9.9720466046668108E-2,2.2080183269549631,0.66032192677338297]
[5,1,7.8,4.2488676407660453,-2.0511395297185247E-2,4.9829071705856789,0,0,8.9847554196775992,0,2.638958750313606,0.28500001514885875,0,0,0,0.20239938418569434,0.20239938418569434,0.19469280321284319,0.19,8.1860022064345311E-2,0,0,0,0,4.2488676407660457E-2,2.7149999848511412,1.3900911095475608,0,1,0.22094922547721726,0.68817365300070699,2.1130812138705828,0,0,0.68817365300070699,0,0,0,0,1.5635949045607226E-2,5.7127656483397127E-2,0.41161713601600342,6.0288971016929892E-2,0,0,0,2.1130812138705828,2.1130812138705828,0.68817365300070699,0.22094922547721726,0,0,0,0,0,0.40636462138328411,0.41161713601600342,5.7127656483397127E-2,1.5635949045607226E-2,0,0,0,2.638958750313606,2.9239587654624648,1.2488676407660453,13.233623060443644,2.1130812138705828,0.22094922547721726,0.21623711437190088,0.25311564114438617]
[5.5,2,7.9999861072487679,3.0222102051178532,9.4184648540779712,5.3856923630976414,0,0,7.5248273030407873,0,1.0878419166460853,0.11748382299907273,0,0,0,8.3433867238124793E-2,8.3433867238124793E-2,0.19274708479986746,0.19,3.374465905864793E-2,0,0,0,0,3.0222102051178534E-2,2.3559913708162297,0.58714682411792463,4.8039918774390511E-2,1,0.11428097593402703,0.39882260261183766,1.9824539973562805,0,0,0.39882260261183766,0,0,0,0,8.181691061472221E-3,3.7538162749173556E-2,0.75879425571588088,3.9163545759397178E-2,0,0,0,1.9824539973562805,1.9824539973562805,0.39882260261183766,0.11428097593402703,0,0,0,0,0,0.75629824987167882,0.75879425571588088,3.7538162749173556E-2,8.181691061472221E-3,0,0,0,1.0878419166460853,1.205325739645158,0.54873501130255065,10.54703750815864,1.9824539973562805,0.11428097593402703,0.32068287547521879,0.23749086371883302]
[6,2,10.250083356498664,2.169094260503698,13.471210437772703,5.866671367092918,0,0,7.0925293889467582,0,0.49699819827847819,6.0193364227755723E-2,0,0,0,4.0846613868145171E-2,4.0846613868145171E-2,0.1913191608346832,0.19,1.7289227585611196E-2,0,0,0,0,2.1690942605036984E-2,2.169094260503698,0.55719156250623381,0,1,6.0161326306893845E-2,0.25687752379043466,0,0,0,0.25687752379043466,0,0,0,0,4.5820607264428293E-3,2.9461194859770043E-2,0,3.0520390996315927E-2,0,0,0,0,0,0.25687752379043466,6.0161326306893845E-2,0,0,0,0,0,0,0,2.9461194859770043E-2,4.5820607264428293E-3,0,0,0,0.49699819827847819,0.55719156250623392,-6.0193364227755897E-2,9.2616236494504562,0,6.0161326306893845E-2,0,0]
[6.5,36,-7.0411861459593581,30.484337959459669,5.2780850062215929,6.6402453190685424,8.0436702536399949,104.75341582045593,14.993770169517253,1.0589186309565459,4.2940337543861498,0.43627920977577606,2.4035603732898521,5.2631852146390337,0.44240186395019976,0.31829755733395204,5.2931230985630497,0.35627645845993844,0.19000000000000014,0.12531166259695264,0.99518451049720036,6.3734120459345595E-2,52.574276917265792,0.43414671121875065,0.30484337959459668,2.5608379621679296,73.388006323535535,0.93036642080595888,0.93130418203000731,2.5172570283410152,3.5553055032715042,3.8298013011981622,7.8093180370692474,110.57612587542329,3.8021108907311207,0,0,0,0,0.12078274552885053,0.17294200809607552,0.19304429275198728,0.17298784204666051,20.751673115392062,52.828672836758038,6.8118412569242563,3.9672053576390969,3.8298013011981622,3.5553055032715042,2.5172570283410152,110.57612587542329,110.57612587542329,7.8093180370692474,0,0,0.20044469583491742,0.19304429275198728,0.17294200809607552,0.12078274552885053,20.751673115392062,20.751673115392062,0.44076511874953817,117.09111982848208,119.9309594115477,28.546139418472507,45.47810812897692,4.1018197981864821,2.6371140829214101,0.18725152918687613,0.20166772099798613]
[7,271,-6.5215819137791078,27.573372148678338,5.3323478659701884,7.0662003087664926,7.5550134740443395,89.50567159290307,14.02168824167614,1.0647245464717638,3.121082755977334,0.31744130618210653,2.6063791678716934,4.4959644291915088,0.41552574107243867,0.23146982925756227,4.5108365176366902,0.32786125813451489,0.18999999999999947,9.1178073498098491E-2,1.0155488452051573,4.9175701266606975E-2,60.31582591058239,9.2337358929828514E-2,0.2757337214867831,2.6698502606884253,59.97888031224506,0.5579445656885017,0.92458694193340529,2.3570827040473743,3.345865796869167,3.6224052921654954,7.1447721626814022,94.091723680930116,3.6002947191123775,0,0,0,0,0.11289643986997469,0.16255825722836023,0.18337879295982334,0.16258960815219256,17.57006945846172,59.392343554285283,1.8777029417276596,3.7674469519724316,3.6224052921654954,3.345865796869167,2.3570827040473743,94.091723680930116,94.091723680930116,7.1447721626814022,0,0,0.19126250100203224,0.18337879295982334,0.16255825722836023,0.11289643986997469,17.57006945846172,17.57006945846172,0.40471299002918831,100.18176782292474,103.10558829697854,25.650805128279572,41.595060390354476,3.9055993494908301,2.4787940522112528,0.17793880666221265,0.20016022613252341]
[7.5,1041,-3.6273399084647271,22.303652351738521,6.1154874257299721,7.5505014614738633,7.0268158392849003,69.555186852758169,12.987059083453744,1.0173398289775222,2.1037282465901885,0.21395119728546155,2.7780209203683399,3.505530250084929,0.38647487116067042,0.15601290764450551,3.5211063789260169,0.28234549224996397,0.1899999999999982,6.1452802805407512E-2,0.94284627267708898,7.4493556300432404E-2,46.534465672831175,0.150903995833473,0.22303652351738509,2.7843204485575166,44.931870863455089,0.62249213826467975,0.91069771157409618,2.1871912416376822,3.2135356351340008,3.5418829771673956,6.0587797770846734,77.344588993155313,3.5023253909336569,0,0,0,0,0.10473927632490038,0.15652633272455019,0.18211132280670111,0.15654868549043538,15.058355867336132,49.355305335940535,2.0257322019219677,3.7118623139850806,3.5418829771673956,3.2135356351340008,2.1871912416376822,77.344588993155313,77.344588993155313,6.0587797770846734,0,0,0.19163348841826727,0.18211132280670111,0.15652633272455019,0.10473927632490038,15.058355867336132,15.058355867336132,0.34482044907702647,78.685730938633256,81.677703056287058,20.322720534873067,35.290711435192264,3.871810902659973,2.3144249502104737,0.17545458270629355,0.21505965603755475]
[8,2951,0.71646430629359581,18.838658405575497,6.7897360586838165,8.0389630307381736,8.5594676452811207,56.899907175400621,13.329631324385328,0.98428148039573959,2.0234208992252007,0.20593269951882195,2.7894102974310733,2.872027469464502,0.4707707204904637,0.15012025069236817,2.8892086945585618,0.25107135743355719,0.19000000000000283,5.9149664667827923E-2,0.9292558670506269,5.502561334511219E-2,39.759367537750109,0.15821245017054544,0.18838658405575526,2.7940130217421184,34.25461462466771,0.71374836003336084,0.87316074335734517,2.0316144854695111,3.1433838196076,3.5287341949233597,5.0626153175334538,68.56046472882413,3.5553827596851288,0,0,0,0,9.6263900445057934E-2,0.15204821617232761,0.18296969115640341,0.15207786465563247,13.761232512828682,42.786243216244308,2.8752510068040729,3.7202094165758148,3.5287341949233597,3.1433838196076,2.0316144854695111,68.56046472882413,68.56046472882413,5.0626153175334538,0,0,0.19399149053892095,0.18296969115640341,0.15204821617232761,9.6263900445057934E-2,13.761232512828682,13.761232512828682,0.28764278463380499,67.482795719906946,70.478138716856847,16.822994164710298,32.168289729960826,4.0113427526157048,2.1909196699137872,0.17538878805268146,0.2316952276615698]
[8.5,7336,2.7765456079707138,15.913120472779555,7.4450098467727468,8.5212861987749875,8.2870194435506139,47.29654335425468,13.279647924181813,0.99201476031052882,1.9164731535499375,0.19739489832334342,2.799357362218271,2.389920521669386,0.45578606939528615,0.14313889921090869,2.407998368577565,0.22820801682597325,0.19000000000003375,5.6697367976272665E-2,0.93979805867604871,5.2216701634482839E-2,34.15185142219886,0.16373065411075791,0.15913120472779585,2.8023481914232269,27.531138023565791,0.51053310265523677,0.85587801283182863,1.913926466066372,3.1147391514542853,3.5758982006643563,4.3299367784178626,57.962883468947688,3.5786042156871081,0,0,0,0,8.9713720833684285E-2,0.14978483496708578,0.1877717906647775,0.14982302169292916,11.550261071759074,36.339563704047947,3.1355993194835108,3.8110104775893943,3.5758982006643563,3.1147391514542853,1.913926466066372,57.962883468947688,57.962883468947688,4.3299367784178626,0,0,0.2018454905540478,0.1877717906647775,0.14978483496708578,8.9713720833684285E-2,11.550261071759074,11.550261071759074,0.24607254534903178,57.50003595135523,60.496788211896842,13.905392143343514,29.19276839696137,4.13508913366966,2.0723210416109032,0.1780108920089026,0.25574870768312236]
[9,7811,4.6981658913645505,12.992645680866216,8.0779247074422305,8.9778785506672332,8.580242496449376,38.743664306428236,12.984636102037753,1.0081271408660961,1.8195317844766028,0.18976355788131116,2.8067875081455855,1.9603347226161669,0.47191333730471369,0.13685550791942569,1.9820156316513238,0.203490205908957,0.190000000000035,5.4505432313957207E-2,0.96669088243971613,4.1436258426381004E-2,28.78725090863065,0.16609825115849114,0.12992645680866238,2.8099868633055038,21.451575683831912,0.46964448992200764,0.82540410799301944,1.8371719644691136,3.1508506166520664,3.7471748568572294,3.7847374544167507,48.747262716421254,3.7240794002776942,0,0,0,0,8.5067327095352682E-2,0.15068200094458914,0.20179519273445912,0.15073357114490146,9.5705287428405086,29.779168741074635,4.0085243568406321,4.0592035678162626,3.7471748568572294,3.1508506166520664,1.8371719644691136,48.747262716421254,48.747262716421254,3.7847374544167507,0,0,0.22184592974809866,0.20179519273445912,0.15068200094458914,8.5067327095352682E-2,9.5705287428405086,9.5705287428405086,0.21540161722654844,49.143438587354218,52.139989653381114,11.001022400545496,25.977281782903969,4.4671701227439913,2.0071380096317548,0.18779443100271459,0.2984486476124823]
[9.5,4714,6.6557330133081303,10.317243084799726,8.8555962676717765,9.4789220240066321,9.1467747332153362,27.428028693531129,12.772372581825392,1.0136964791139509,1.8203317485369239,0.19529293973080417,2.779084737077703,1.396167471403676,0.5030726103268448,0.13914499077775166,1.4303999195286647,0.17408630208878376,0.19000000000002218,5.6093626335508982E-2,0.84955991959931831,0.16413655951463041,20.652804593130213,0.5440457431726019,0.10317243084799695,2.8040672521922496,13.22066337958735,1.4506570427251839,0.76177256073046695,1.6073687471255553,2.9057113116909012,3.6153323209604746,3.0061082958007526,37.876362369181457,3.6510222844929707,0,0,0,0,7.2705198609040761E-2,0.13681552558866916,0.20506543562421634,0.13690900013522078,7.3986086776113495,24.310003469644361,3.3145920980761634,3.9968336293737097,3.6153323209604746,2.9057113116909012,1.6073687471255553,37.876362369181457,37.876362369181457,3.0061082958007526,0,0,0.23292329387839425,0.20506543562421634,0.13681552558866916,7.2705198609040761E-2,7.3986086776113495,7.3986086776113495,0.17127672727530663,38.395135175283386,41.369512852091894,8.3315793719906228,23.089615666625118,4.6083861727779265,1.7916934369717314,0.18568386190149916,0.35348997680720962]
[10,3638,9.1625617492548752,8.0765998557625185,9.5648314919901125,9.979127716600777,10.851208024029328,18.485966237078721,13.245331479227206,1.0163726195054135,2.2306631349635171,0.24497136591280944,2.5682504433712361,0.9601336607465405,0.59681644132161482,0.17283688443336842,1.0265688587458013,0.13920565368358886,0.1900000000000126,7.0362667904706244E-2,0.65232885837101529,0.36404376113439951,14.158626314785847,0.97308792194032623,8.0765998557624882E-2,2.7497057930364854,7.5522801341927579,3.7851541024984701,0.6562574785252886,1.4031799496262425,2.6910935805246448,3.6035658818049741,2.3833180351567447,31.059315048680752,3.7810583171640522,0,0,0,0,6.2316785566059352E-2,0.1249811683562301,0.22860580587628077,0.12523997762572484,6.0522888545181424,21.704737009707852,2.6729971114134181,4.0765337467713234,3.6035658818049741,2.6910935805246448,1.4031799496262425,31.059315048680752,31.059315048680752,2.3833180351567447,0,0,0.27189604256424349,0.22860580587628077,0.1249811683562301,6.2316785566059352E-2,6.0522888545181424,6.0522888545181424,0.13546746490995448,31.567837396071564,34.381059205355612,6.0982953163186373,21.321931334989724,5.1765019171174123,1.6124739670714348,0.20173068159760449,0.42655788150330165]
[10.5,4188,11.46452979327818,5.8009465298326166,10.356166442847218,10.525463622254309,10.131846841974497,8.8800565265301312,12.191123723578013,1.013071194183601,1.5336410147023123,0.17561460686804131,1.9265729952259909,0.48553079908116781,0.55725157630860034,0.12181460027308702,0.55309176016473738,9.6848837108265612E-2,0.19000000000001813,5.0441455540031155E-2,0.36713696355918785,0.64593423062441102,7.1309778437328459,1.6284484975290234,5.8009465298326186E-2,2.8026530416747573,3.1821780727926523,6.7360774490081461,0.50685916844063561,1.0447203668994824,1.9821081640939926,3.1214591706797084,1.6852871686857884,20.280454622701889,3.3236972521333978,0,0,0,0,4.69335740919294E-2,9.2717451588731958E-2,0.26058451911648861,9.3060939601317699E-2,3.9637496766944595,19.423208642905355,2.5210747787043837,3.6892958707629977,3.1214591706797084,1.9821081640939926,1.0447203668994824,20.280454622701889,20.280454622701889,1.6852871686857884,0,0,0.34179202144507387,0.26058451911648861,9.2717451588731958E-2,4.69335740919294E-2,3.9637496766944595,3.9637496766944595,9.634030210508604E-2,20.545544383206941,22.647731985300972,3.8357500754734186,17.992070253410631,5.3563303080092242,1.2587618693300622,0.22638852165451392,0.49228044806505084]
[11,6498,14.650491357622874,3.8059659695426,10.999816611591694,11.007317086350056,11.448576788616871,2.449657205866306,11.138115691246462,1.0119404014939846,1.0023585116979234,0.11776573728930448,0.76352732988576955,0.13276980923735074,0.62967172337392696,8.0862033623800747E-2,0.19470806512360794,5.1584988321533465E-2,0.19000000000003106,3.3825632773707461E-2,0.14252990110249963,0.86941050039148415,2.4185640062473892,2.0270199514854008,3.8059659695426039E-2,2.7783694877679626,0.73370818401952764,10.652040401051499,0.23166969475423585,0.67852881057190151,1.0724944941112859,3.0167930368575528,1.3378019154435252,14.724772806958311,3.2756729496095756,0,0,0,0,3.0976966848491189E-2,5.0097868442563497E-2,0.57086143613526807,5.0792561175828387E-2,2.8808709042763341,16.968818385049545,2.3314877731205916,3.7941295548513736,3.0167930368575528,1.0724944941112859,0.67852881057190151,14.724772806958311,14.724772806958311,1.3378019154435252,0,0,0.88684342257441062,0.57086143613526807,5.0097868442563497E-2,3.0976966848491189E-2,2.8808709042763341,2.8808709042763341,7.7036877090282646E-2,14.9005925061811,15.781885573356174,1.9217711459793174,14.944081660789061,7.75357281087072,1.0560625892968305,0.46335866132132519,0.49932348722923248]
[11.5,4710,16.789973827390209,3.4247706833270057,11.507105297118338,11.464763253953073,18.389427178988349,0.40459067932820886,12.366768447843677,1.0105636945103837,1.2566482805263319,0.15075164039067054,0.19949119787819708,2.1922413488157249E-2,1.0114184948443588,0.10268736058526899,0.11885395503818962,3.8418771889360451E-2,0.19000000000002215,4.3300112114629162E-2,7.9090800316816715E-2,0.93147289419356771,0.93476464514169799,2.1828871683235507,3.4247706833270108E-2,2.7723893459872655,7.4720261072530908E-2,18.315101871665771,8.2852058298269082E-2,0.45208107318379437,0.57331707697326006,2.8379929158158186,1.6213343221720149,19.841071124722525,4.5996326858808274,0,0,0,0,2.6996169125577535E-2,3.4452828707937026E-2,1.0288762191091545,3.6596583433420801E-2,3.8867346019852653,11.818879583937441,2.3434790018376304,3.311683837616187,2.8379929158158186,0.57331707697326006,0.45208107318379437,19.841071124722525,19.841071124722525,1.6213343221720149,0,0,1.3900906677942861,1.0288762191091545,3.4452828707937026E-2,2.6996169125577535E-2,3.8867346019852653,3.8867346019852653,9.2587204178622554E-2,20.050666138842889,20.400908977111758,1.5121933914594536,15.791539131170683,13.259326652321576,1.2918885744862392,0.96632952549801976,0.68905626489461647]
[12,2039,19.667173013185035,3.5490379677952522,12.023363299533328,11.971292819335444,34.377718265300125,7.3331684657678255E-3,13.905546156655928,1.0033271864254041,1.6902484497315271,0.20236732187046633,1.095989311063391E-2,4.1647859855388329E-4,1.8907745045915054,0.13795163921321105,0.13808876761336722,3.7152961755400352E-2,0.18999999999999798,5.8125587904850909E-2,8.1485067231679642E-2,0.92184211919372394,0.94144546609598634,2.2049000952301649,3.5490379677952592E-2,2.7486048502537863,8.4929201475167479E-4,34.282378921214011,4.7056618342176289E-2,0.45461179574490718,0.53136134053577311,2.6307716048485865,2.5943101750253712,35.955668670779673,7.9713788040122564,0,0,0,0,3.3096624034792993E-2,3.8788391300360194E-2,0.89211225367980451,4.2021141112654342E-2,7.0902874480894846,11.553595009245726,2.3918413460633037,2.8384529436141634,2.6307716048485865,0.53136134053577311,0.45461179574490718,35.955668670779673,35.955668670779673,2.5943101750253712,0,0,1.0289738270214475,0.89211225367980451,3.8788391300360194E-2,3.3096624034792993E-2,7.0902874480894846,7.0902874480894846,0.14702425947960618,36.075299883497422,36.288627098478521,1.6013929820964035,17.454584124451181,22.527449718351331,2.0790313214993046,1.6405719662529934,1.1979960268331957]
[12.5,930,21.72286450114953,3.6942481285607673,12.495069407453366,12.46241424642869,53.288810555729889,0,15.07802534724037,0.99080944503513357,2.0514916316567904,0.24112044661127788,0,0,2.93088458056515,0.16554052960680662,0.16554052960680662,3.7877278724939664E-2,0.18999999999999825,6.9256575545985799E-2,9.6714983402337307E-2,0.89409446163279682,1.1274914963911948,2.1306008557726175,3.6942481285607578E-2,2.7220333801040875,1.7191938883167157E-3,52.960941864841971,3.7070481196692352E-2,0.53903255735382827,0.61448020671058412,2.6718250604662166,3.6702619151330209,55.853628025744484,11.863551676983512,0,0,0,0,3.9216341585562232E-2,4.4805607585629383E-2,0.78330314535167511,4.8498575682762016E-2,11.142458508216942,11.657878197639713,2.3829706448261749,2.8060561086011591,2.6718250604662166,0.61448020671058412,0.53903255735382827,55.853628025744484,55.853628025744484,3.6702619151330209,0,0,0.85515622868565322,0.78330314535167511,4.4805607585629383E-2,3.9216341585562232E-2,11.142458508216942,11.142458508216942,0.20709477537941434,55.340302187386676,55.581422633997953,1.7219037468805358,18.772273475801136,32.139021874854038,2.9608253206862005,2.2943137331072618,1.7237648042954623]
[13,464,23.744602722280749,3.7185122805273356,13.060503000260518,12.955257194443107,70.903764712651551,0,16.876794863046502,1.0080202344555247,2.089879607961783,0.24489830916896657,0,0,3.8997070591958352,0.1683277734783972,0.1683277734783972,3.8514699127517163E-2,0.18999999999999878,7.0341683952618361E-2,0.14327814063080707,0.86474209382471734,1.5027537358645879,2.1944802985938594,3.7185122805273314E-2,2.7219756128781207,0,70.573543697625553,2.8630980510882687E-2,0.55567307188792736,0.62304392617920856,2.6776199566588899,4.3250892668275833,72.412876076877922,15.4951949230477,0,0,0,0,4.0384220522616518E-2,4.5373012723744971E-2,0.77454342009385546,4.9102527376015538E-2,14.218177701019618,10.48836709667261,2.5377280859403601,2.7804323507216284,2.6776199566588899,0.62304392617920856,0.55567307188792736,72.412876076877922,72.412876076877922,4.3250892668275833,0,0,0.82712307352060088,0.77454342009385546,4.5373012723744971E-2,4.0384220522616518E-2,14.218177701019618,14.218177701019618,0.24281222005533146,72.993644320613328,73.238542629782287,1.7596585929357731,20.595307143573837,41.481708220929633,3.5560791649875556,2.9489983459354074,2.2423458878807336]
[13.5,165,25.364987249751529,3.5014753297817323,13.493269665065702,13.469883733833289,84.404571639961588,0,17.614344383816416,1.0113805883612634,1.6321361573481468,0.1976363731554924,0,0,4.6422514401978869,0.13414675656959041,0.13414675656959041,3.5277416506289946E-2,0.19000000000000056,5.676672634131464E-2,0.1118241766558517,0.89955641170541123,1.0697327378128851,1.8146634183367534,3.5014753297817301E-2,2.7828651092756385,0,84.304789918325241,1.8970230255593086E-2,0.47704696021343057,0.51972407890751204,3.0215792506520867,4.8844683584339332,85.068577336168502,19.108596803141452,0,0,0,0,3.524805049826138E-2,3.8456948402053111E-2,1.2097810333401871,4.1700316776709608E-2,16.651973224475118,9.5662026746244457,2.0172869591318343,3.1328562184998954,3.0215792506520867,0.51972407890751204,0.47704696021343057,85.068577336168502,85.068577336168502,4.8844683584339332,0,0,1.2936909594376391,1.2097810333401871,3.8456948402053111E-2,3.524805049826138E-2,16.651973224475118,16.651973224475118,0.27376354084991233,86.036707797309731,86.234344170465221,1.5323544357118648,21.11581971359815,56.146741114330275,4.083873860456011,4.2303685298910727,3.063985237601734]
[14,110,27.714326281770138,3.4389979740406766,14.382108836762287,13.969588230639243,92.517715600098882,0,16.713244720239928,0.99439833890105167,1.0495200949013768,0.1288120662381918,0,0,5.0884743580054357,8.6981118813190234E-2,8.6981118813190234E-2,3.7471012642383311E-2,0.19000000000000017,3.6998449206764948E-2,6.3912679109792384E-2,0.9304856597912593,0.58792086109803832,2.1968721303452177,3.4389979740406751E-2,2.8626374647720207,0,92.910142287128934,1.1216747904389117E-2,0.32492572313335327,0.34153051774828014,2.2880198355646577,5.5983884195562146,94.094320188029528,21.134146633299185,0,0,0,0,2.4218924483475558E-2,2.5482218188963804E-2,1.0493634384179718,2.7646727289840859E-2,18.708654164630609,9.1988142147519518,2.3609951504658904,2.3450424445559674,2.2880198355646577,0.34153051774828014,0.32492572313335327,94.094320188029528,94.094320188029528,5.5983884195562146,0,0,1.0981915132067297,1.0493634384179718,2.5482218188963804E-2,2.4218924483475558E-2,18.708654164630609,18.708654164630609,0.31441999965780637,93.567235695000264,93.696047761238461,1.4419467819315157,20.152242694280606,64.889520797477104,4.6494104493804196,4.998424032338348,3.5682386690089207]
[14.5,31,27.692086214058929,3.2977589452157168,15.075274781553611,14.374901458249369,99.24062881490353,0,16.454678402065174,0.97574805140482024,0.95903542580153289,0.11806590681451226,0,0,5.4582345848196949,7.963571286584667E-2,7.963571286584667E-2,3.8322779142794618E-2,0.19000000000000011,3.3911849905814348E-2,3.309574158123664E-2,0.9426523098235835,0.48795692818064101,2.1538256201589072,3.2977589452157174E-2,2.868390001811711,0,99.568644477096328,9.5712439065433006E-3,0.31172885287403057,0.32569379877212912,2.9909835570334145,6.0894331564772077,102.69009924892387,23.474333896457924,0,0,0,0,2.33056240185875E-2,2.4374210752346172E-2,1.9360028620449998,2.6443374181238054E-2,20.778400075384432,14.743797989324531,2.2848568848910937,3.0807133663337383,2.9909835570334145,0.32569379877212912,0.31172885287403057,102.69009924892387,102.69009924892387,6.0894331564772077,0,0,2.0498668907539566,1.9360028620449998,2.4374210752346172E-2,2.33056240185875E-2,20.778400075384432,20.778400075384432,0.34222019267255327,100.19966424070506,100.31773014751957,1.2870510879943136,19.752437347280889,77.852126598060707,5.0787519729219266,6.3594569700153825,4.2886486393638048]
[15,1,12.79988888893276,2.8482909633729983,34.989330369568762,14.889330369568762,0,0,7.2744884715907059,0,0,0,0,0,0,0,0,0.19212307550422783,0.19,0,0,0,0,0,2.8482909633729982E-2,2.8482909633729983,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,10.122779434963704,0,0,0,0]
[15.5,5,12.41998891046428,3.1600210487578564,34.405244818465327,15.534119602898073,0,0,7.2764230283917515,0,9.5826889211748173E-2,1.163888888888889E-2,0,0,0,7.8893260019277309E-3,7.8893260019277309E-3,0.19268064654564648,0.19,3.3430163179158806E-3,0,0,0,0,3.1600210487578564E-2,2.9151981360862722,0.1034324503153754,0.24078958488632268,1,1.0297164178355663E-2,3.4007931099977892E-2,0.4109496339296787,0,0,3.4007931099977892E-2,0,0,0,0,7.7947858660635866E-4,3.2454464067109053E-3,0.35877581060707264,3.4135165019766739E-3,0,0,0,0.4109496339296787,0.4109496339296787,3.4007931099977892E-2,1.0297164178355663E-2,0,0,0,0,0,0.35848926106024803,0.35877581060707264,3.2454464067109053E-3,7.7947858660635866E-4,0,0,0,9.5826889211748173E-2,0.10746577810063707,0.23318402378269543,10.436444077149607,0.4109496339296787,1.0297164178355663E-2,0.1400419700778428,5.3859103431546089E-2]
[16,1,12.399944444448916,2.9162761849140173,36.472430668912303,16.172267536720064,0,0,7.2972297376751971,0,0,0,0,0,0,0,0,0.1922250417574923,0.19,0,0,0,0,0,2.9162761849140174E-2,2.9162761849140173,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,10.213505922589214,0,0,0,0]
[16.5,1,12.10016666665325,2.9020818424273389,35.92561702127373,16.392680851064647,0,0,7.3839226416726458,0,0,0,0,0,0,0,0,0.19220355850507723,0.19,0,0,0,0,0,2.9020818424273391E-2,2.9020818424273389,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,10.286004484099985,0,0,0,0]
[17,4,9.875097206799671,3.1925121876736133,33.111694291773361,17.006492476208901,0,0,7.2966583710532955,0,0,0,0,0,0,0,0,0.19274786838393282,0.19,0,0,0,0,0,3.1925121876736136E-2,2.8941118732644679,0,0.29840031440914516,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0.29840031440914538,10.489170558726908,0,0,0,0]
[17.5,5,10.260055552468948,2.9214305717575764,35.637381633934488,17.437223989982471,0,0,7.1734413198506743,0,7.1967631555650445E-3,8.7291666666666659E-4,0,0,0,5.9199553782704755E-4,5.9199553782704755E-4,0.19223343571026594,0.19,2.5072622384369103E-4,0,0,0,0,2.9214305717575766E-2,2.9214305717575764,8.0696798222317338E-3,0,1,7.9938407429815356E-4,2.7622357006337724E-3,0,0,0,2.7622357006337724E-3,0,0,0,0,6.0586683823810394E-5,2.7221055725186997E-4,0,2.8541932611988807E-4,0,0,0,0,0,2.7622357006337724E-3,7.9938407429815356E-4,0,0,0,0,0,0,0,2.7221055725186997E-4,6.0586683823810394E-5,0,0,0,7.1967631555650445E-3,8.0696798222317113E-3,-8.729166666667787E-4,10.09487189160825,0,7.9938407429815356E-4,0,0]
[18,13,9.6540619420856064,3.027226572395862,34.930148331530368,17.991731715368211,0,0,6.9543297871840748,0,7.1044969612629294E-2,8.6172542735042761E-3,0,0,0,5.844058514446495E-3,5.844058514446495E-3,0.19243015191826268,0.18999999999999997,2.475117850764643E-3,0,0,0,0,3.0272265723958629E-2,2.8972077115185821,0,5.0356636991146862E-2,1,7.9809421513386183E-3,2.6315249942816758E-2,0.58520617313164702,0,0,2.6315249942816758E-2,0,0,0,0,6.0536498403044496E-4,2.5544039963357515E-3,0.97653753748789429,2.6820664691775318E-3,0,0,0,0.58520617313164702,0.58520617313164702,2.6315249942816758E-2,7.9809421513386183E-3,0,0,0,0,0,0.97632468864606736,0.97653753748789429,2.5544039963357515E-3,6.0536498403044496E-4,0,0,0,7.1044969612629294E-2,7.9662223886133574E-2,0.12140160660377575,9.9815563595799368,0.58520617313164702,7.9809421513386183E-3,0.3743882845468639,7.6616804403872849E-2]
[18.5,11,10.154338416770516,2.9570446265918076,34.902223490588987,18.506220133857045,0,0,7.181654010570977,0,0.30560428891923336,3.7016511112625404E-2,0,0,0,2.5116714774237502E-2,2.5116714774237502E-2,0.19229823222222081,0.18999999999999997,1.0632183352137387E-2,0,0,0,0,2.9570446265918073E-2,2.8811135698526393,0.26668974329269096,0,1,3.3793370559018591E-2,0.11586595513330221,7.8532148840198097,0,0,0.11586595513330221,0,0,0,0,2.5588845261276549E-3,1.1354260041580886E-2,40.862495402755826,1.1909960369980549E-2,0,0,0,7.8532148840198097,7.8532148840198097,0.11586595513330221,3.3793370559018591E-2,0,0,0,0,0,40.861581981821836,40.862495402755826,1.1354260041580886E-2,2.5588845261276549E-3,0,0,0,0.30560428891923336,0.34262080003185874,3.8914545626542729E-2,10.138698637162785,7.8532148840198097,3.3793370559018591E-2,15.570145925688353,1.0270965791079898]
[19,7,11.25719045303687,2.9644062435708025,37.007184147133842,18.98046429365375,0,0,6.9730203897615555,0,0.13719716897914641,1.6618093116747799E-2,0,0,0,1.1275830497237545E-2,1.1275830497237545E-2,0.19231239871187153,0.18999999999999997,4.7731838487580069E-3,0,0,0,0,2.9644062435708027E-2,2.8879137142917046,0.15309110321950922,7.5768370402713253E-2,1,1.5478379642065818E-2,5.1887376242540445E-2,2.2914147969115772,0,0,5.1887376242540445E-2,0,0,0,0,1.173555158364389E-3,5.0793000823028218E-3,7.7425447281400714,5.3284070209295709E-3,0,0,0,2.2914147969115772,2.2914147969115772,5.1887376242540445E-2,1.5478379642065818E-2,0,0,0,0,0,7.7421343055623373,7.7425447281400714,5.0793000823028218E-3,1.173555158364389E-3,0,0,0,0.13719716897914641,0.15381526209589422,5.9874436162349998E-2,9.9374266333323575,2.2914147969115772,1.5478379642065818E-2,2.9528867990690766,0.29968195543985493]
[19.5,1,8.6999722222157256,3.9887544634311998,21.59949916489596,19.28597662772173,0,0,7.6583872681182434,0,2.812137249092526,0.34062188753761963,0,0,0,0.23112126286333876,0.23112126286333876,0.19414174259276193,0.19,9.783618858709435E-2,0,0,0,0,3.9887544634311996E-2,2.6593781124623805,1.8233827856613263,0,1,0.27068951415694054,0.79041193573947999,2.8441209148465223,0,0,0.79041193573947999,0,0,0,0,2.0350108695593845E-2,6.9551745517536137E-2,0.69839503782166978,7.3750039481602886E-2,0,0,0,2.8441209148465223,2.8441209148465223,0.79041193573947999,0.27068951415694054,0,0,0,0,0,0.69134994006461437,0.69839503782166978,6.9551745517536137E-2,2.0350108695593845E-2,0,0,0,2.812137249092526,3.1527591366301455,0.98875446343119977,11.647141731549443,2.8441209148465223,0.27068951415694054,0.34299354707287494,0.37193295078782446]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Figure 9 for B&W"]

{"sheet":"Plot","index":1,"n_rows":44,"n_cols":70,"rows_kept":44,"cut":false,"hidden":false,"merged":[]}
[]
["HP EFT / BH ExFT (°C)","Count","ODA Temperature (°C)","EL 007 (kW)","GHE EFT (°C)","GHE ExFT (°C)","Clg Provided (kW)","Bldg Htg Provided (kW)","EL 003 (kW)","CP Energy (kW)","DHW Provided by HP (kW)","DHW by LPS (kW)","Useful Bldg Htg by LPS (kW)","Bldg Htg Uncertainty (kW)","Bldg Clg Uncertainty (kW)","DHW Htg by HP Uncertainty (kW)","Bldg + DHW Htg by HP Uncertainty (kW)","EL007+EL011 Uncertainty (kW)","EL011 Uncertainty (kW)","LPS DHW Uncertainty (kW)","CP Power for Heat Extraction from GHE (kW)","CP Power for Heat Rejection to GHE (kW)","Heat Extraction by GHE (kW)","Heat Rejection to GHE (kW)","EL007 Uncertainty (kW)","LPS Electricity going to bldg heat (kW)","Alt Calc GHE Heat Extraction (kW)","Alt Calc GHE Heat Extraction (kW)","HtgFrac","COP H4","COP H3","COP H2","COP C3","COP C2","Overall (H+C) COP","Not used","Not used","Not used","Not used","Error COP H4","Error COP H3","Error COP H2","Error COP H3b","Error COP C2","BPF0, heating","BPF0, cooling","BPF1*, heating","BPF2, heating","BPF3+, heating","BPF4+, heating","BPF2, cooling","BPF3, cooling","BPF4, cooling","Error BPF0, heating","Error BPF0, cooling","Error BPF1*, heating","Error BPF2, heating","Error BPF3+, heating","Error BPF4+, heating","Error BPF2, cooling","Error BPF3, cooling","Error BPF4, cooling","Htg & Clg Provided Boundary 2","Htg & Clg Provided Boundary 4+","Electricity Used Boundary 2","Electricity Used Boundary 4+","BPFHC2","BPFHC4+","Error BPFHC2","Error BPFHC4+"]
[3,2,7.9499444521628249,3.5188290633289467,11.417540168328188,3.1339850249538559,0,0,8.9706886849089216,0,1.8947127785524307,0.2046235737962967,0,0,0,0.14531818640295352,0.14531818640295352,0.19337051826053631,0.19,5.8773646931566184E-2,0,0,0,0,3.5188290633289473E-2,2.7953764262037035,1.375883715223484,0,1,0.16808786333202658,0.59660083356327487,3.6519017774282809,0,0,0.59660083356327487,0,0,0,0,1.1922703489092594E-2,5.2728816308009463E-2,1.518394834290101,5.5310988198773559E-2,0,0,0,3.6519017774282809,3.6519017774282809,0.59660083356327487,0.16808786333202658,0,0,0,0,0,1.5141632054743852,1.518394834290101,5.2728816308009463E-2,1.1922703489092594E-2,0,0,0,1.8947127785524307,2.0993363523487272,0.51882906332894674,12.489517748237869,3.6519017774282809,0.16808786333202658,0.63391163531794925,0.43749102886998698]
[4,1,8.1,2.7307073424787487,17.11909394108671,3.7610169489606995,0,0,7.4028826839064372,0,1.5988462543792068,0.17267083339768741,0,0,0,0.12262620522412453,0.12262620522412453,0.19195227599334877,0.19,4.9595920984147307E-2,0,0,0,0,2.7307073424787488E-2,2.7307073424787487,1.7715170877768942,0,1,0.17481633687215811,0.64873926993906006,0,0,0,0.64873926993906006,0,0,0,0,1.25458641922163E-2,6.4001315103745349E-2,0,6.6528470672524515E-2,0,0,0,0,0,0.64873926993906006,0.17481633687215811,0,0,0,0,0,0,0,6.4001315103745349E-2,1.25458641922163E-2,0,0,0,1.5988462543792068,1.7715170877768942,-0.17267083339768741,10.133590026385185,0,0.17481633687215811,0,0]
[4.5,1,7.8,3.1990883824346859,-0.70075041712599073,4.6563368541610197,0,0,8.9930558740221986,4.0036248068627855E-7,1.09730093713965,0.11850537022243837,0,0,0,8.4159342739653503E-2,8.4159342739653503E-2,0.19267437984294347,0.19,3.403807615969897E-2,4.0036248068627855E-7,0,1.2456346052757565,0,3.1990883824346859E-2,2.8814946297775617,0.89821215434248347,0,1,9.9720466046668108E-2,0.38004769167394964,5.511616082647862,0,0,0.38004769167394964,0,0,0,0,7.0803555264690766E-3,3.4871208961912509E-2,5.7041102100577019,3.6458322706675282E-2,0,3111267.0776256574,0,5.5116271663899692,5.511616082647862,0.38004769167394964,9.9720466046668108E-2,0,0,0,0,0,5.701570270272696,5.7041102100577019,3.4871208961912509E-2,7.0803555264690766E-3,0,0,0,1.09730093713965,1.2158063073620884,0.19908878279716655,12.192144256456885,5.511616082647862,9.9720466046668108E-2,2.2080183269549631,0.66032192677338297]
[5,1,7.8,4.2488676407660453,-2.0511395297185247E-2,4.9829071705856789,0,0,8.9847554196775992,0,2.638958750313606,0.28500001514885875,0,0,0,0.20239938418569434,0.20239938418569434,0.19469280321284319,0.19,8.1860022064345311E-2,0,0,0,0,4.2488676407660457E-2,2.7149999848511412,1.3900911095475608,0,1,0.22094922547721726,0.68817365300070699,2.1130812138705828,0,0,0.68817365300070699,0,0,0,0,1.5635949045607226E-2,5.7127656483397127E-2,0.41161713601600342,6.0288971016929892E-2,0,0,0,2.1130812138705828,2.1130812138705828,0.68817365300070699,0.22094922547721726,0,0,0,0,0,0.40636462138328411,0.41161713601600342,5.7127656483397127E-2,1.5635949045607226E-2,0,0,0,2.638958750313606,2.9239587654624648,1.2488676407660453,13.233623060443644,2.1130812138705828,0.22094922547721726,0.21623711437190088,0.25311564114438617]
[5.5,2,7.9999861072487679,3.0222102051178532,9.4184648540779712,5.3856923630976414,0,0,7.5248273030407873,0,1.0878419166460853,0.11748382299907273,0,0,0,8.3433867238124793E-2,8.3433867238124793E-2,0.19274708479986746,0.19,3.374465905864793E-2,0,0,0,0,3.0222102051178534E-2,2.3559913708162297,0.58714682411792463,4.8039918774390511E-2,1,0.11428097593402703,0.39882260261183766,1.9824539973562805,0,0,0.39882260261183766,0,0,0,0,8.181691061472221E-3,3.7538162749173556E-2,0.75879425571588088,3.9163545759397178E-2,0,0,0,1.9824539973562805,1.9824539973562805,0.39882260261183766,0.11428097593402703,0,0,0,0,0,0.75629824987167882,0.75879425571588088,3.7538162749173556E-2,8.181691061472221E-3,0,0,0,1.0878419166460853,1.205325739645158,0.54873501130255065,10.54703750815864,1.9824539973562805,0.11428097593402703,0.32068287547521879,0.23749086371883302]
[6,2,10.250083356498664,2.169094260503698,13.471210437772703,5.866671367092918,0,0,7.0925293889467582,0,0.49699819827847819,6.0193364227755723E-2,0,0,0,4.0846613868145171E-2,4.0846613868145171E-2,0.1913191608346832,0.19,1.7289227585611196E-2,0,0,0,0,2.1690942605036984E-2,2.169094260503698,0.55719156250623381,0,1,6.0161326306893845E-2,0.25687752379043466,0,0,0,0.25687752379043466,0,0,0,0,4.5820607264428293E-3,2.9461194859770043E-2,0,3.0520390996315927E-2,0,0,0,0,0,0.25687752379043466,6.0161326306893845E-2,0,0,0,0,0,0,0,2.9461194859770043E-2,4.5820607264428293E-3,0,0,0,0.49699819827847819,0.55719156250623392,-6.0193364227755897E-2,9.2616236494504562,0,6.0161326306893845E-2,0,0]
[6.5,36,-7.0411861459593581,30.484337959459669,5.2780850062215929,6.6402453190685424,8.0436702536399949,104.75341582045593,14.993770169517253,1.0589186309565459,4.2940337543861498,0.43627920977577606,2.4035603732898521,5.2631852146390337,0.44240186395019976,0.31829755733395204,5.2931230985630497,0.35627645845993844,0.19000000000000014,0.12531166259695264,0.99518451049720036,6.3734120459345595E-2,52.574276917265792,0.43414671121875065,0.30484337959459668,2.5608379621679296,73.388006323535535,0.93036642080595888,0.93130418203000731,2.5172570283410152,3.5553055032715042,3.8298013011981622,7.8093180370692474,110.57612587542329,3.8021108907311207,0,0,0,0,0.12078274552885053,0.17294200809607552,0.19304429275198728,0.17298784204666051,20.751673115392062,52.828672836758038,6.8118412569242563,3.9672053576390969,3.8298013011981622,3.5553055032715042,2.5172570283410152,110.57612587542329,110.57612587542329,7.8093180370692474,0,0,0.20044469583491742,0.19304429275198728,0.17294200809607552,0.12078274552885053,20.751673115392062,20.751673115392062,0.44076511874953817,117.09111982848208,119.9309594115477,28.546139418472507,45.47810812897692,4.1018197981864821,2.6371140829214101,0.18725152918687613,0.20166772099798613]
[7,271,-6.5215819137791078,27.573372148678338,5.3323478659701884,7.0662003087664926,7.5550134740443395,89.50567159290307,14.02168824167614,1.0647245464717638,3.121082755977334,0.31744130618210653,2.6063791678716934,4.4959644291915088,0.41552574107243867,0.23146982925756227,4.5108365176366902,0.32786125813451489,0.18999999999999947,9.1178073498098491E-2,1.0155488452051573,4.9175701266606975E-2,60.31582591058239,9.2337358929828514E-2,0.2757337214867831,2.6698502606884253,59.97888031224506,0.5579445656885017,0.92458694193340529,2.3570827040473743,3.345865796869167,3.6224052921654954,7.1447721626814022,94.091723680930116,3.6002947191123775,0,0,0,0,0.11289643986997469,0.16255825722836023,0.18337879295982334,0.16258960815219256,17.57006945846172,59.392343554285283,1.8777029417276596,3.7674469519724316,3.6224052921654954,3.345865796869167,2.3570827040473743,94.091723680930116,94.091723680930116,7.1447721626814022,0,0,0.19126250100203224,0.18337879295982334,0.16255825722836023,0.11289643986997469,17.57006945846172,17.57006945846172,0.40471299002918831,100.18176782292474,103.10558829697854,25.650805128279572,41.595060390354476,3.9055993494908301,2.4787940522112528,0.17793880666221265,0.20016022613252341]
[7.5,1041,-3.6273399084647271,22.303652351738521,6.1154874257299721,7.5505014614738633,7.0268158392849003,69.555186852758169,12.987059083453744,1.0173398289775222,2.1037282465901885,0.21395119728546155,2.7780209203683399,3.505530250084929,0.38647487116067042,0.15601290764450551,3.5211063789260169,0.28234549224996397,0.1899999999999982,6.1452802805407512E-2,0.94284627267708898,7.4493556300432404E-2,46.534465672831175,0.150903995833473,0.22303652351738509,2.7843204485575166,44.931870863455089,0.62249213826467975,0.91069771157409618,2.1871912416376822,3.2135356351340008,3.5418829771673956,6.0587797770846734,77.344588993155313,3.5023253909336569,0,0,0,0,0.10473927632490038,0.15652633272455019,0.18211132280670111,0.15654868549043538,15.058355867336132,49.355305335940535,2.0257322019219677,3.7118623139850806,3.5418829771673956,3.2135356351340008,2.1871912416376822,77.344588993155313,77.344588993155313,6.0587797770846734,0,0,0.19163348841826727,0.18211132280670111,0.15652633272455019,0.10473927632490038,15.058355867336132,15.058355867336132,0.34482044907702647,78.685730938633256,81.677703056287058,20.322720534873067,35.290711435192264,3.871810902659973,2.3144249502104737,0.17545458270629355,0.21505965603755475]
[8,2951,0.71646430629359581,18.838658405575497,6.7897360586838165,8.0389630307381736,8.5594676452811207,56.899907175400621,13.329631324385328,0.98428148039573959,2.0234208992252007,0.20593269951882195,2.7894102974310733,2.872027469464502,0.4707707204904637,0.15012025069236817,2.8892086945585618,0.25107135743355719,0.19000000000000283,5.9149664667827923E-2,0.9292558670506269,5.502561334511219E-2,39.759367537750109,0.15821245017054544,0.18838658405575526,2.7940130217421184,34.25461462466771,0.71374836003336084,0.87316074335734517,2.0316144854695111,3.1433838196076,3.5287341949233597,5.0626153175334538,68.56046472882413,3.5553827596851288,0,0,0,0,9.6263900445057934E-2,0.15204821617232761,0.18296969115640341,0.15207786465563247,13.761232512828682,42.786243216244308,2.8752510068040729,3.7202094165758148,3.5287341949233597,3.1433838196076,2.0316144854695111,68.56046472882413,68.56046472882413,5.0626153175334538,0,0,0.19399149053892095,0.18296969115640341,0.15204821617232761,9.6263900445057934E-2,13.761232512828682,13.761232512828682,0.28764278463380499,67.482795719906946,70.478138716856847,16.822994164710298,32.168289729960826,4.0113427526157048,2.1909196699137872,0.17538878805268146,0.2316952276615698]
[8.5,7336,2.7765456079707138,15.913120472779555,7.4450098467727468,8.5212861987749875,8.2870194435506139,47.29654335425468,13.279647924181813,0.99201476031052882,1.9164731535499375,0.19739489832334342,2.799357362218271,2.389920521669386,0.45578606939528615,0.14313889921090869,2.407998368577565,0.22820801682597325,0.19000000000003375,5.6697367976272665E-2,0.93979805867604871,5.2216701634482839E-2,34.15185142219886,0.16373065411075791,0.15913120472779585,2.8023481914232269,27.531138023565791,0.51053310265523677,0.85587801283182863,1.913926466066372,3.1147391514542853,3.5758982006643563,4.3299367784178626,57.962883468947688,3.5786042156871081,0,0,0,0,8.9713720833684285E-2,0.14978483496708578,0.1877717906647775,0.14982302169292916,11.550261071759074,36.339563704047947,3.1355993194835108,3.8110104775893943,3.5758982006643563,3.1147391514542853,1.913926466066372,57.962883468947688,57.962883468947688,4.3299367784178626,0,0,0.2018454905540478,0.1877717906647775,0.14978483496708578,8.9713720833684285E-2,11.550261071759074,11.550261071759074,0.24607254534903178,57.50003595135523,60.496788211896842,13.905392143343514,29.19276839696137,4.13508913366966,2.0723210416109032,0.1780108920089026,0.25574870768312236]
[9,7811,4.6981658913645505,12.992645680866216,8.0779247074422305,8.9778785506672332,8.580242496449376,38.743664306428236,12.984636102037753,1.0081271408660961,1.8195317844766028,0.18976355788131116,2.8067875081455855,1.9603347226161669,0.47191333730471369,0.13685550791942569,1.9820156316513238,0.203490205908957,0.190000000000035,5.4505432313957207E-2,0.96669088243971613,4.1436258426381004E-2,28.78725090863065,0.16609825115849114,0.12992645680866238,2.8099868633055038,21.451575683831912,0.46964448992200764,0.82540410799301944,1.8371719644691136,3.1508506166520664,3.7471748568572294,3.7847374544167507,48.747262716421254,3.7240794002776942,0,0,0,0,8.5067327095352682E-2,0.15068200094458914,0.20179519273445912,0.15073357114490146,9.5705287428405086,29.779168741074635,4.0085243568406321,4.0592035678162626,3.7471748568572294,3.1508506166520664,1.8371719644691136,48.747262716421254,48.747262716421254,3.7847374544167507,0,0,0.22184592974809866,0.20179519273445912,0.15068200094458914,8.5067327095352682E-2,9.5705287428405086,9.5705287428405086,0.21540161722654844,49.143438587354218,52.139989653381114,11.001022400545496,25.977281782903969,4.4671701227439913,2.0071380096317548,0.18779443100271459,0.2984486476124823]
[9.5,4714,6.6557330133081303,10.317243084799726,8.8555962676717765,9.4789220240066321,9.1467747332153362,27.428028693531129,12.772372581825392,1.0136964791139509,1.8203317485369239,0.19529293973080417,2.779084737077703,1.396167471403676,0.5030726103268448,0.13914499077775166,1.4303999195286647,0.17408630208878376,0.19000000000002218,5.6093626335508982E-2,0.84955991959931831,0.16413655951463041,20.652804593130213,0.5440457431726019,0.10317243084799695,2.8040672521922496,13.22066337958735,1.4506570427251839,0.76177256073046695,1.6073687471255553,2.9057113116909012,3.6153323209604746,3.0061082958007526,37.876362369181457,3.6510222844929707,0,0,0,0,7.2705198609040761E-2,0.13681552558866916,0.20506543562421634,0.13690900013522078,7.3986086776113495,24.310003469644361,3.3145920980761634,3.9968336293737097,3.6153323209604746,2.9057113116909012,1.6073687471255553,37.876362369181457,37.876362369181457,3.0061082958007526,0,0,0.23292329387839425,0.20506543562421634,0.13681552558866916,7.2705198609040761E-2,7.3986086776113495,7.3986086776113495,0.17127672727530663,38.395135175283386,41.369512852091894,8.3315793719906228,23.089615666625118,4.6083861727779265,1.7916934369717314,0.18568386190149916,0.35348997680720962]
[10,3638,9.1625617492548752,8.0765998557625185,9.5648314919901125,9.979127716600777,10.851208024029328,18.485966237078721,13.245331479227206,1.0163726195054135,2.2306631349635171,0.24497136591280944,2.5682504433712361,0.9601336607465405,0.59681644132161482,0.17283688443336842,1.0265688587458013,0.13920565368358886,0.1900000000000126,7.0362667904706244E-2,0.65232885837101529,0.36404376113439951,14.158626314785847,0.97308792194032623,8.0765998557624882E-2,2.7497057930364854,7.5522801341927579,3.7851541024984701,0.6562574785252886,1.4031799496262425,2.6910935805246448,3.6035658818049741,2.3833180351567447,31.059315048680752,3.7810583171640522,0,0,0,0,6.2316785566059352E-2,0.1249811683562301,0.22860580587628077,0.12523997762572484,6.0522888545181424,21.704737009707852,2.6729971114134181,4.0765337467713234,3.6035658818049741,2.6910935805246448,1.4031799496262425,31.059315048680752,31.059315048680752,2.3833180351567447,0,0,0.27189604256424349,0.22860580587628077,0.1249811683562301,6.2316785566059352E-2,6.0522888545181424,6.0522888545181424,0.13546746490995448,31.567837396071564,34.381059205355612,6.0982953163186373,21.321931334989724,5.1765019171174123,1.6124739670714348,0.20173068159760449,0.42655788150330165]
[10.5,4188,11.46452979327818,5.8009465298326166,10.356166442847218,10.525463622254309,10.131846841974497,8.8800565265301312,12.191123723578013,1.013071194183601,1.5336410147023123,0.17561460686804131,1.9265729952259909,0.48553079908116781,0.55725157630860034,0.12181460027308702,0.55309176016473738,9.6848837108265612E-2,0.19000000000001813,5.0441455540031155E-2,0.36713696355918785,0.64593423062441102,7.1309778437328459,1.6284484975290234,5.8009465298326186E-2,2.8026530416747573,3.1821780727926523,6.7360774490081461,0.50685916844063561,1.0447203668994824,1.9821081640939926,3.1214591706797084,1.6852871686857884,20.280454622701889,3.3236972521333978,0,0,0,0,4.69335740919294E-2,9.2717451588731958E-2,0.26058451911648861,9.3060939601317699E-2,3.9637496766944595,19.423208642905355,2.5210747787043837,3.6892958707629977,3.1214591706797084,1.9821081640939926,1.0447203668994824,20.280454622701889,20.280454622701889,1.6852871686857884,0,0,0.34179202144507387,0.26058451911648861,9.2717451588731958E-2,4.69335740919294E-2,3.9637496766944595,3.9637496766944595,9.634030210508604E-2,20.545544383206941,22.647731985300972,3.8357500754734186,17.992070253410631,5.3563303080092242,1.2587618693300622,0.22638852165451392,0.49228044806505084]
[11,6498,14.650491357622874,3.8059659695426,10.999816611591694,11.007317086350056,11.448576788616871,2.449657205866306,11.138115691246462,1.0119404014939846,1.0023585116979234,0.11776573728930448,0.76352732988576955,0.13276980923735074,0.62967172337392696,8.0862033623800747E-2,0.19470806512360794,5.1584988321533465E-2,0.19000000000003106,3.3825632773707461E-2,0.14252990110249963,0.86941050039148415,2.4185640062473892,2.0270199514854008,3.8059659695426039E-2,2.7783694877679626,0.73370818401952764,10.652040401051499,0.23166969475423585,0.67852881057190151,1.0724944941112859,3.0167930368575528,1.3378019154435252,14.724772806958311,3.2756729496095756,0,0,0,0,3.0976966848491189E-2,5.0097868442563497E-2,0.57086143613526807,5.0792561175828387E-2,2.8808709042763341,16.968818385049545,2.3314877731205916,3.7941295548513736,3.0167930368575528,1.0724944941112859,0.67852881057190151,14.724772806958311,14.724772806958311,1.3378019154435252,0,0,0.88684342257441062,0.57086143613526807,5.0097868442563497E-2,3.0976966848491189E-2,2.8808709042763341,2.8808709042763341,7.7036877090282646E-2,14.9005925061811,15.781885573356174,1.9217711459793174,14.944081660789061,7.75357281087072,1.0560625892968305,0.46335866132132519,0.49932348722923248]
[11.5,4710,16.789973827390209,3.4247706833270057,11.507105297118338,11.464763253953073,18.389427178988349,0.40459067932820886,12.366768447843677,1.0105636945103837,1.2566482805263319,0.15075164039067054,0.19949119787819708,2.1922413488157249E-2,1.0114184948443588,0.10268736058526899,0.11885395503818962,3.8418771889360451E-2,0.19000000000002215,4.3300112114629162E-2,7.9090800316816715E-2,0.93147289419356771,0.93476464514169799,2.1828871683235507,3.4247706833270108E-2,2.7723893459872655,7.4720261072530908E-2,18.315101871665771,8.2852058298269082E-2,0.45208107318379437,0.57331707697326006,2.8379929158158186,1.6213343221720149,19.841071124722525,4.5996326858808274,0,0,0,0,2.6996169125577535E-2,3.4452828707937026E-2,1.0288762191091545,3.6596583433420801E-2,3.8867346019852653,11.818879583937441,2.3434790018376304,3.311683837616187,2.8379929158158186,0.57331707697326006,0.45208107318379437,19.841071124722525,19.841071124722525,1.6213343221720149,0,0,1.3900906677942861,1.0288762191091545,3.4452828707937026E-2,2.6996169125577535E-2,3.8867346019852653,3.8867346019852653,9.2587204178622554E-2,20.050666138842889,20.400908977111758,1.5121933914594536,15.791539131170683,13.259326652321576,1.2918885744862392,0.96632952549801976,0.68905626489461647]
[12,2039,19.667173013185035,3.5490379677952522,12.023363299533328,11.971292819335444,34.377718265300125,7.3331684657678255E-3,13.905546156655928,1.0033271864254041,1.6902484497315271,0.20236732187046633,1.095989311063391E-2,4.1647859855388329E-4,1.8907745045915054,0.13795163921321105,0.13808876761336722,3.7152961755400352E-2,0.18999999999999798,5.8125587904850909E-2,8.1485067231679642E-2,0.92184211919372394,0.94144546609598634,2.2049000952301649,3.5490379677952592E-2,2.7486048502537863,8.4929201475167479E-4,34.282378921214011,4.7056618342176289E-2,0.45461179574490718,0.53136134053577311,2.6307716048485865,2.5943101750253712,35.955668670779673,7.9713788040122564,0,0,0,0,3.3096624034792993E-2,3.8788391300360194E-2,0.89211225367980451,4.2021141112654342E-2,7.0902874480894846,11.553595009245726,2.3918413460633037,2.8384529436141634,2.6307716048485865,0.53136134053577311,0.45461179574490718,35.955668670779673,35.955668670779673,2.5943101750253712,0,0,1.0289738270214475,0.89211225367980451,3.8788391300360194E-2,3.3096624034792993E-2,7.0902874480894846,7.0902874480894846,0.14702425947960618,36.075299883497422,36.288627098478521,1.6013929820964035,17.454584124451181,22.527449718351331,2.0790313214993046,1.6405719662529934,1.1979960268331957]
[12.5,930,21.72286450114953,3.6942481285607673,12.495069407453366,12.46241424642869,53.288810555729889,0,15.07802534724037,0.99080944503513357,2.0514916316567904,0.24112044661127788,0,0,2.93088458056515,0.16554052960680662,0.16554052960680662,3.7877278724939664E-2,0.18999999999999825,6.9256575545985799E-2,9.6714983402337307E-2,0.89409446163279682,1.1274914963911948,2.1306008557726175,3.6942481285607578E-2,2.7220333801040875,1.7191938883167157E-3,52.960941864841971,3.7070481196692352E-2,0.53903255735382827,0.61448020671058412,2.6718250604662166,3.6702619151330209,55.853628025744484,11.863551676983512,0,0,0,0,3.9216341585562232E-2,4.4805607585629383E-2,0.78330314535167511,4.8498575682762016E-2,11.142458508216942,11.657878197639713,2.3829706448261749,2.8060561086011591,2.6718250604662166,0.61448020671058412,0.53903255735382827,55.853628025744484,55.853628025744484,3.6702619151330209,0,0,0.85515622868565322,0.78330314535167511,4.4805607585629383E-2,3.9216341585562232E-2,11.142458508216942,11.142458508216942,0.20709477537941434,55.340302187386676,55.581422633997953,1.7219037468805358,18.772273475801136,32.139021874854038,2.9608253206862005,2.2943137331072618,1.7237648042954623]
[13,464,23.744602722280749,3.7185122805273356,13.060503000260518,12.955257194443107,70.903764712651551,0,16.876794863046502,1.0080202344555247,2.089879607961783,0.24489830916896657,0,0,3.8997070591958352,0.1683277734783972,0.1683277734783972,3.8514699127517163E-2,0.18999999999999878,7.0341683952618361E-2,0.14327814063080707,0.86474209382471734,1.5027537358645879,2.1944802985938594,3.7185122805273314E-2,2.7219756128781207,0,70.573543697625553,2.8630980510882687E-2,0.55567307188792736,0.62304392617920856,2.6776199566588899,4.3250892668275833,72.412876076877922,15.4951949230477,0,0,0,0,4.0384220522616518E-2,4.5373012723744971E-2,0.77454342009385546,4.9102527376015538E-2,14.218177701019618,10.48836709667261,2.5377280859403601,2.7804323507216284,2.6776199566588899,0.62304392617920856,0.55567307188792736,72.412876076877922,72.412876076877922,4.3250892668275833,0,0,0.82712307352060088,0.77454342009385546,4.5373012723744971E-2,4.0384220522616518E-2,14.218177701019618,14.218177701019618,0.24281222005533146,72.993644320613328,73.238542629782287,1.7596585929357731,20.595307143573837,41.481708220929633,3.5560791649875556,2.9489983459354074,2.2423458878807336]
[13.5,165,25.364987249751529,3.5014753297817323,13.493269665065702,13.469883733833289,84.404571639961588,0,17.614344383816416,1.0113805883612634,1.6321361573481468,0.1976363731554924,0,0,4.6422514401978869,0.13414675656959041,0.13414675656959041,3.5277416506289946E-2,0.19000000000000056,5.676672634131464E-2,0.1118241766558517,0.89955641170541123,1.0697327378128851,1.8146634183367534,3.5014753297817301E-2,2.7828651092756385,0,84.304789918325241,1.8970230255593086E-2,0.47704696021343057,0.51972407890751204,3.0215792506520867,4.8844683584339332,85.068577336168502,19.108596803141452,0,0,0,0,3.524805049826138E-2,3.8456948402053111E-2,1.2097810333401871,4.1700316776709608E-2,16.651973224475118,9.5662026746244457,2.0172869591318343,3.1328562184998954,3.0215792506520867,0.51972407890751204,0.47704696021343057,85.068577336168502,85.068577336168502,4.8844683584339332,0,0,1.2936909594376391,1.2097810333401871,3.8456948402053111E-2,3.524805049826138E-2,16.651973224475118,16.651973224475118,0.27376354084991233,86.036707797309731,86.234344170465221,1.5323544357118648,21.11581971359815,56.146741114330275,4.083873860456011,4.2303685298910727,3.063985237601734]
[14,110,27.714326281770138,3.4389979740406766,14.382108836762287,13.969588230639243,92.517715600098882,0,16.713244720239928,0.99439833890105167,1.0495200949013768,0.1288120662381918,0,0,5.0884743580054357,8.6981118813190234E-2,8.6981118813190234E-2,3.7471012642383311E-2,0.19000000000000017,3.6998449206764948E-2,6.3912679109792384E-2,0.9304856597912593,0.58792086109803832,2.1968721303452177,3.4389979740406751E-2,2.8626374647720207,0,92.910142287128934,1.1216747904389117E-2,0.32492572313335327,0.34153051774828014,2.2880198355646577,5.5983884195562146,94.094320188029528,21.134146633299185,0,0,0,0,2.4218924483475558E-2,2.5482218188963804E-2,1.0493634384179718,2.7646727289840859E-2,18.708654164630609,9.1988142147519518,2.3609951504658904,2.3450424445559674,2.2880198355646577,0.34153051774828014,0.32492572313335327,94.094320188029528,94.094320188029528,5.5983884195562146,0,0,1.0981915132067297,1.0493634384179718,2.5482218188963804E-2,2.4218924483475558E-2,18.708654164630609,18.708654164630609,0.31441999965780637,93.567235695000264,93.696047761238461,1.4419467819315157,20.152242694280606,64.889520797477104,4.6494104493804196,4.998424032338348,3.5682386690089207]
[14.5,31,27.692086214058929,3.2977589452157168,15.075274781553611,14.374901458249369,99.24062881490353,0,16.454678402065174,0.97574805140482024,0.95903542580153289,0.11806590681451226,0,0,5.4582345848196949,7.963571286584667E-2,7.963571286584667E-2,3.8322779142794618E-2,0.19000000000000011,3.3911849905814348E-2,3.309574158123664E-2,0.9426523098235835,0.48795692818064101,2.1538256201589072,3.2977589452157174E-2,2.868390001811711,0,99.568644477096328,9.5712439065433006E-3,0.31172885287403057,0.32569379877212912,2.9909835570334145,6.0894331564772077,102.69009924892387,23.474333896457924,0,0,0,0,2.33056240185875E-2,2.4374210752346172E-2,1.9360028620449998,2.6443374181238054E-2,20.778400075384432,14.743797989324531,2.2848568848910937,3.0807133663337383,2.9909835570334145,0.32569379877212912,0.31172885287403057,102.69009924892387,102.69009924892387,6.0894331564772077,0,0,2.0498668907539566,1.9360028620449998,2.4374210752346172E-2,2.33056240185875E-2,20.778400075384432,20.778400075384432,0.34222019267255327,100.19966424070506,100.31773014751957,1.2870510879943136,19.752437347280889,77.852126598060707,5.0787519729219266,6.3594569700153825,4.2886486393638048]
[15,1,12.79988888893276,2.8482909633729983,34.989330369568762,14.889330369568762,0,0,7.2744884715907059,0,0,0,0,0,0,0,0,0.19212307550422783,0.19,0,0,0,0,0,2.8482909633729982E-2,2.8482909633729983,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,10.122779434963704,0,0,0,0]
[15.5,5,12.41998891046428,3.1600210487578564,34.405244818465327,15.534119602898073,0,0,7.2764230283917515,0,9.5826889211748173E-2,1.163888888888889E-2,0,0,0,7.8893260019277309E-3,7.8893260019277309E-3,0.19268064654564648,0.19,3.3430163179158806E-3,0,0,0,0,3.1600210487578564E-2,2.9151981360862722,0.1034324503153754,0.24078958488632268,1,1.0297164178355663E-2,3.4007931099977892E-2,0.4109496339296787,0,0,3.4007931099977892E-2,0,0,0,0,7.7947858660635866E-4,3.2454464067109053E-3,0.35877581060707264,3.4135165019766739E-3,0,0,0,0.4109496339296787,0.4109496339296787,3.4007931099977892E-2,1.0297164178355663E-2,0,0,0,0,0,0.35848926106024803,0.35877581060707264,3.2454464067109053E-3,7.7947858660635866E-4,0,0,0,9.5826889211748173E-2,0.10746577810063707,0.23318402378269543,10.436444077149607,0.4109496339296787,1.0297164178355663E-2,0.1400419700778428,5.3859103431546089E-2]
[16,1,12.399944444448916,2.9162761849140173,36.472430668912303,16.172267536720064,0,0,7.2972297376751971,0,0,0,0,0,0,0,0,0.1922250417574923,0.19,0,0,0,0,0,2.9162761849140174E-2,2.9162761849140173,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,10.213505922589214,0,0,0,0]
[16.5,1,12.10016666665325,2.9020818424273389,35.92561702127373,16.392680851064647,0,0,7.3839226416726458,0,0,0,0,0,0,0,0,0.19220355850507723,0.19,0,0,0,0,0,2.9020818424273391E-2,2.9020818424273389,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,10.286004484099985,0,0,0,0]
[17,4,9.875097206799671,3.1925121876736133,33.111694291773361,17.006492476208901,0,0,7.2966583710532955,0,0,0,0,0,0,0,0,0.19274786838393282,0.19,0,0,0,0,0,3.1925121876736136E-2,2.8941118732644679,0,0.29840031440914516,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0,0.29840031440914538,10.489170558726908,0,0,0,0]
[17.5,5,10.260055552468948,2.9214305717575764,35.637381633934488,17.437223989982471,0,0,7.1734413198506743,0,7.1967631555650445E-3,8.7291666666666659E-4,0,0,0,5.9199553782704755E-4,5.9199553782704755E-4,0.19223343571026594,0.19,2.5072622384369103E-4,0,0,0,0,2.9214305717575766E-2,2.9214305717575764,8.0696798222317338E-3,0,1,7.9938407429815356E-4,2.7622357006337724E-3,0,0,0,2.7622357006337724E-3,0,0,0,0,6.0586683823810394E-5,2.7221055725186997E-4,0,2.8541932611988807E-4,0,0,0,0,0,2.7622357006337724E-3,7.9938407429815356E-4,0,0,0,0,0,0,0,2.7221055725186997E-4,6.0586683823810394E-5,0,0,0,7.1967631555650445E-3,8.0696798222317113E-3,-8.729166666667787E-4,10.09487189160825,0,7.9938407429815356E-4,0,0]
[18,13,9.6540619420856064,3.027226572395862,34.930148331530368,17.991731715368211,0,0,6.9543297871840748,0,7.1044969612629294E-2,8.6172542735042761E-3,0,0,0,5.844058514446495E-3,5.844058514446495E-3,0.19243015191826268,0.18999999999999997,2.475117850764643E-3,0,0,0,0,3.0272265723958629E-2,2.8972077115185821,0,5.0356636991146862E-2,1,7.9809421513386183E-3,2.6315249942816758E-2,0.58520617313164702,0,0,2.6315249942816758E-2,0,0,0,0,6.0536498403044496E-4,2.5544039963357515E-3,0.97653753748789429,2.6820664691775318E-3,0,0,0,0.58520617313164702,0.58520617313164702,2.6315249942816758E-2,7.9809421513386183E-3,0,0,0,0,0,0.97632468864606736,0.97653753748789429,2.5544039963357515E-3,6.0536498403044496E-4,0,0,0,7.1044969612629294E-2,7.9662223886133574E-2,0.12140160660377575,9.9815563595799368,0.58520617313164702,7.9809421513386183E-3,0.3743882845468639,7.6616804403872849E-2]
[18.5,11,10.154338416770516,2.9570446265918076,34.902223490588987,18.506220133857045,0,0,7.181654010570977,0,0.30560428891923336,3.7016511112625404E-2,0,0,0,2.5116714774237502E-2,2.5116714774237502E-2,0.19229823222222081,0.18999999999999997,1.0632183352137387E-2,0,0,0,0,2.9570446265918073E-2,2.8811135698526393,0.26668974329269096,0,1,3.3793370559018591E-2,0.11586595513330221,7.8532148840198097,0,0,0.11586595513330221,0,0,0,0,2.5588845261276549E-3,1.1354260041580886E-2,40.862495402755826,1.1909960369980549E-2,0,0,0,7.8532148840198097,7.8532148840198097,0.11586595513330221,3.3793370559018591E-2,0,0,0,0,0,40.861581981821836,40.862495402755826,1.1354260041580886E-2,2.5588845261276549E-3,0,0,0,0.30560428891923336,0.34262080003185874,3.8914545626542729E-2,10.138698637162785,7.8532148840198097,3.3793370559018591E-2,15.570145925688353,1.0270965791079898]
[19,7,11.25719045303687,2.9644062435708025,37.007184147133842,18.98046429365375,0,0,6.9730203897615555,0,0.13719716897914641,1.6618093116747799E-2,0,0,0,1.1275830497237545E-2,1.1275830497237545E-2,0.19231239871187153,0.18999999999999997,4.7731838487580069E-3,0,0,0,0,2.9644062435708027E-2,2.8879137142917046,0.15309110321950922,7.5768370402713253E-2,1,1.5478379642065818E-2,5.1887376242540445E-2,2.2914147969115772,0,0,5.1887376242540445E-2,0,0,0,0,1.173555158364389E-3,5.0793000823028218E-3,7.7425447281400714,5.3284070209295709E-3,0,0,0,2.2914147969115772,2.2914147969115772,5.1887376242540445E-2,1.5478379642065818E-2,0,0,0,0,0,7.7421343055623373,7.7425447281400714,5.0793000823028218E-3,1.173555158364389E-3,0,0,0,0.13719716897914641,0.15381526209589422,5.9874436162349998E-2,9.9374266333323575,2.2914147969115772,1.5478379642065818E-2,2.9528867990690766,0.29968195543985493]
[19.5,1,8.6999722222157256,3.9887544634311998,21.59949916489596,19.28597662772173,0,0,7.6583872681182434,0,2.812137249092526,0.34062188753761963,0,0,0,0.23112126286333876,0.23112126286333876,0.19414174259276193,0.19,9.783618858709435E-2,0,0,0,0,3.9887544634311996E-2,2.6593781124623805,1.8233827856613263,0,1,0.27068951415694054,0.79041193573947999,2.8441209148465223,0,0,0.79041193573947999,0,0,0,0,2.0350108695593845E-2,6.9551745517536137E-2,0.69839503782166978,7.3750039481602886E-2,0,0,0,2.8441209148465223,2.8441209148465223,0.79041193573947999,0.27068951415694054,0,0,0,0,0,0.69134994006461437,0.69839503782166978,6.9551745517536137E-2,2.0350108695593845E-2,0,0,0,2.812137249092526,3.1527591366301455,0.98875446343119977,11.647141731549443,2.8441209148465223,0.27068951415694054,0.34299354707287494,0.37193295078782446]
[]
[]
[null,null,null,null,null,null,null,null,null,null,{"$f":"CELL(\"filename\")","v":"/Users/signhildgehlin/Dropbox/Gehlin-Spitler_collaboration/Studenthuset/studenthuset data detailed excel files/2021_update/20211208_Results/[BinResultsHPEFT_V2.xlsm]Plot (2)"}]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Figure 9 for B&W"]

{"sheet":"Plot (2)","index":2,"n_rows":39,"n_cols":76,"rows_kept":39,"cut":false,"hidden":false,"merged":[]}
[]
["HP EFT / BH ExFT (°C)","Count","ODA Temperature (°C)","EL 007 (kW)","GHE EFT (°C)","GHE ExFT (°C)","Clg Provided (kW)","Bldg Htg Provided (kW)","EL 003 (kW)","CP Energy (kW)","DHW Provided by HP (kW)","DHW by LPS (kW)","Useful Bldg Htg by LPS (kW)","Bldg Htg Uncertainty (kW)","Bldg Clg Uncertainty (kW)","DHW Htg by HP Uncertainty (kW)","Bldg + DHW Htg by HP Uncertainty (kW)","EL007+EL011 Uncertainty (kW)","EL011 Uncertainty (kW)","LPS DHW Uncertainty (kW)","CP Power for Heat Extraction from GHE (kW)","CP Power for Heat Rejection to GHE (kW)","Heat Extraction by GHE (kW)","Heat Rejection to GHE (kW)","EL007 Uncertainty (kW)","LPS Electricity going to bldg heat (kW)","Alt Calc GHE Heat Extraction (kW)","Alt Calc GHE Heat Extraction (kW)","HtgFrac","COP H4","COP H3","COP H2","COP C3","COP C2","Overall (H+C) COP","Not used","Not used","Not used","Not used","Error COP H4","Error COP H3","Error COP H2","Error COP H3b","Error COP C2","BPF0, heating","BPF0, cooling","BPF1*, heating","BPF2, heating","BPF3+, heating","BPF4+, heating","BPF2, cooling","BPF3, cooling","BPF4, cooling","Error BPF0, heating","Error BPF0, cooling","Error BPF1*, heating","Error BPF2, heating","Error BPF3+, heating","Error BPF4+, heating","Error BPF2, cooling","Error BPF3, cooling","Error BPF4, cooling","Htg & Clg Provided Boundary 2","Htg & Clg Provided Boundary 4+","Electricity Used Boundary 2","Electricity Used Boundary 4+","BPFHC2","BPFHC4+","Error BPFHC2","Error BPFHC4+",null,null,"BPF2* w/all CP power allocated to cooling","BPF4* w/all pumping power allocated to cooling","Difference BPF2*","Difference BPF2*"]
[6.5,36,-7.0411861459593581,30.484337959459669,5.2780850062215929,6.6402453190685424,8.0436702536399949,104.75341582045593,14.993770169517253,1.0589186309565459,4.2940337543861498,0.43627920977577606,2.4035603732898521,5.2631852146390337,0.44240186395019976,0.31829755733395204,5.2931230985630497,0.35627645845993844,0.19000000000000014,0.12531166259695264,0.99518451049720036,6.3734120459345595E-2,52.574276917265792,0.43414671121875065,0.30484337959459668,2.5608379621679296,73.388006323535535,0.93036642080595888,0.93130418203000731,2.5172570283410152,3.5553055032715042,3.8298013011981622,7.8093180370692474,110.57612587542329,3.8021108907311207,0,0,0,0,0.12078274552885053,0.17294200809607552,0.19304429275198728,0.17298784204666051,20.751673115392062,52.828672836758038,6.8118412569242563,3.9672053576390969,3.8298013011981622,3.5553055032715042,2.5172570283410152,110.57612587542329,110.57612587542329,7.8093180370692474,0,0,0.20044469583491742,0.19304429275198728,0.17294200809607552,0.12078274552885053,20.751673115392062,20.751673115392062,0.44076511874953817,117.09111982848208,119.9309594115477,28.546139418472507,45.47810812897692,4.1018197981864821,2.6371140829214101,0.18725152918687613,0.20166772099798613,null,null,{"$f":"G3/J3","v":7.5961174149650761},{"$f":"G3/(I3)","v":0.53646749034428964},{"$f":"(BU3-AY3)/AY3","v":-0.93130418203000731},{"$f":"(BV3-BA3)/BA3","v":-0.93130418203000731}]
[7,271,-6.5215819137791078,27.573372148678338,5.3323478659701884,7.0662003087664926,7.5550134740443395,89.50567159290307,14.02168824167614,1.0647245464717638,3.121082755977334,0.31744130618210653,2.6063791678716934,4.4959644291915088,0.41552574107243867,0.23146982925756227,4.5108365176366902,0.32786125813451489,0.18999999999999947,9.1178073498098491E-2,1.0155488452051573,4.9175701266606975E-2,60.31582591058239,9.2337358929828514E-2,0.2757337214867831,2.6698502606884253,59.97888031224506,0.5579445656885017,0.92458694193340529,2.3570827040473743,3.345865796869167,3.6224052921654954,7.1447721626814022,94.091723680930116,3.6002947191123775,0,0,0,0,0.11289643986997469,0.16255825722836023,0.18337879295982334,0.16258960815219256,17.57006945846172,59.392343554285283,1.8777029417276596,3.7674469519724316,3.6224052921654954,3.345865796869167,2.3570827040473743,94.091723680930116,94.091723680930116,7.1447721626814022,0,0,0.19126250100203224,0.18337879295982334,0.16255825722836023,0.11289643986997469,17.57006945846172,17.57006945846172,0.40471299002918831,100.18176782292474,103.10558829697854,25.650805128279572,41.595060390354476,3.9055993494908301,2.4787940522112528,0.17793880666221265,0.20016022613252341,null,null,{"$f":"G4/J4","v":7.0957446215359665},{"$f":"G4/(I4)","v":0.53880911797688213},{"$f":"(BU4-AY4)/AY4","v":-0.92458694193340529},{"$f":"(BV4-BA4)/BA4","v":-0.92458694193340529}]
[7.5,1041,-3.6273399084647271,22.303652351738521,6.1154874257299721,7.5505014614738633,7.0268158392849003,69.555186852758169,12.987059083453744,1.0173398289775222,2.1037282465901885,0.21395119728546155,2.7780209203683399,3.505530250084929,0.38647487116067042,0.15601290764450551,3.5211063789260169,0.28234549224996397,0.1899999999999982,6.1452802805407512E-2,0.94284627267708898,7.4493556300432404E-2,46.534465672831175,0.150903995833473,0.22303652351738509,2.7843204485575166,44.931870863455089,0.62249213826467975,0.91069771157409618,2.1871912416376822,3.2135356351340008,3.5418829771673956,6.0587797770846734,77.344588993155313,3.5023253909336569,0,0,0,0,0.10473927632490038,0.15652633272455019,0.18211132280670111,0.15654868549043538,15.058355867336132,49.355305335940535,2.0257322019219677,3.7118623139850806,3.5418829771673956,3.2135356351340008,2.1871912416376822,77.344588993155313,77.344588993155313,6.0587797770846734,0,0,0.19163348841826727,0.18211132280670111,0.15652633272455019,0.10473927632490038,15.058355867336132,15.058355867336132,0.34482044907702647,78.685730938633256,81.677703056287058,20.322720534873067,35.290711435192264,3.871810902659973,2.3144249502104737,0.17545458270629355,0.21505965603755475,null,null,6.9070487944497412,0.54106289916224881,-0.91069771157409629,-0.91069771157409618]
[8,2951,0.71646430629359581,18.838658405575497,6.7897360586838165,8.0389630307381736,8.5594676452811207,56.899907175400621,13.329631324385328,0.98428148039573959,2.0234208992252007,0.20593269951882195,2.7894102974310733,2.872027469464502,0.4707707204904637,0.15012025069236817,2.8892086945585618,0.25107135743355719,0.19000000000000283,5.9149664667827923E-2,0.9292558670506269,5.502561334511219E-2,39.759367537750109,0.15821245017054544,0.18838658405575526,2.7940130217421184,34.25461462466771,0.71374836003336084,0.87316074335734517,2.0316144854695111,3.1433838196076,3.5287341949233597,5.0626153175334538,68.56046472882413,3.5553827596851288,0,0,0,0,9.6263900445057934E-2,0.15204821617232761,0.18296969115640341,0.15207786465563247,13.761232512828682,42.786243216244308,2.8752510068040729,3.7202094165758148,3.5287341949233597,3.1433838196076,2.0316144854695111,68.56046472882413,68.56046472882413,5.0626153175334538,0,0,0.19399149053892095,0.18296969115640341,0.15204821617232761,9.6263900445057934E-2,13.761232512828682,13.761232512828682,0.28764278463380499,67.482795719906946,70.478138716856847,16.822994164710298,32.168289729960826,4.0113427526157048,2.1909196699137872,0.17538878805268146,0.2316952276615698,null,null,8.6961583812790089,0.64213836354366127,-0.87316074335734517,-0.87316074335734517]
[8.5,7336,2.7765456079707138,15.913120472779555,7.4450098467727468,8.5212861987749875,8.2870194435506139,47.29654335425468,13.279647924181813,0.99201476031052882,1.9164731535499375,0.19739489832334342,2.799357362218271,2.389920521669386,0.45578606939528615,0.14313889921090869,2.407998368577565,0.22820801682597325,0.19000000000003375,5.6697367976272665E-2,0.93979805867604871,5.2216701634482839E-2,34.15185142219886,0.16373065411075791,0.15913120472779585,2.8023481914232269,27.531138023565791,0.51053310265523677,0.85587801283182863,1.913926466066372,3.1147391514542853,3.5758982006643563,4.3299367784178626,57.962883468947688,3.5786042156871081,0,0,0,0,8.9713720833684285E-2,0.14978483496708578,0.1877717906647775,0.14982302169292916,11.550261071759074,36.339563704047947,3.1355993194835108,3.8110104775893943,3.5758982006643563,3.1147391514542853,1.913926466066372,57.962883468947688,57.962883468947688,4.3299367784178626,0,0,0.2018454905540478,0.1877717906647775,0.14978483496708578,8.9713720833684285E-2,11.550261071759074,11.550261071759074,0.24607254534903178,57.50003595135523,60.496788211896842,13.905392143343514,29.19276839696137,4.13508913366966,2.0723210416109032,0.1780108920089026,0.25574870768312236,null,null,8.353725947541891,0.62403909281813241,-0.85587801283182863,-0.85587801283182863]
[9,7811,4.6981658913645505,12.992645680866216,8.0779247074422305,8.9778785506672332,8.580242496449376,38.743664306428236,12.984636102037753,1.0081271408660961,1.8195317844766028,0.18976355788131116,2.8067875081455855,1.9603347226161669,0.47191333730471369,0.13685550791942569,1.9820156316513238,0.203490205908957,0.190000000000035,5.4505432313957207E-2,0.96669088243971613,4.1436258426381004E-2,28.78725090863065,0.16609825115849114,0.12992645680866238,2.8099868633055038,21.451575683831912,0.46964448992200764,0.82540410799301944,1.8371719644691136,3.1508506166520664,3.7471748568572294,3.7847374544167507,48.747262716421254,3.7240794002776942,0,0,0,0,8.5067327095352682E-2,0.15068200094458914,0.20179519273445912,0.15073357114490146,9.5705287428405086,29.779168741074635,4.0085243568406321,4.0592035678162626,3.7471748568572294,3.1508506166520664,1.8371719644691136,48.747262716421254,48.747262716421254,3.7847374544167507,0,0,0.22184592974809866,0.20179519273445912,0.15068200094458914,8.5067327095352682E-2,9.5705287428405086,9.5705287428405086,0.21540161722654844,49.143438587354218,52.139989653381114,11.001022400545496,25.977281782903969,4.4671701227439913,2.0071380096317548,0.18779443100271459,0.2984486476124823,null,null,8.5110718168721942,0.66079961186612157,-0.82540410799301944,-0.82540410799301944]
[9.5,4714,6.6557330133081303,10.317243084799726,8.8555962676717765,9.4789220240066321,9.1467747332153362,27.428028693531129,12.772372581825392,1.0136964791139509,1.8203317485369239,0.19529293973080417,2.779084737077703,1.396167471403676,0.5030726103268448,0.13914499077775166,1.4303999195286647,0.17408630208878376,0.19000000000002218,5.6093626335508982E-2,0.84955991959931831,0.16413655951463041,20.652804593130213,0.5440457431726019,0.10317243084799695,2.8040672521922496,13.22066337958735,1.4506570427251839,0.76177256073046695,1.6073687471255553,2.9057113116909012,3.6153323209604746,3.0061082958007526,37.876362369181457,3.6510222844929707,0,0,0,0,7.2705198609040761E-2,0.13681552558866916,0.20506543562421634,0.13690900013522078,7.3986086776113495,24.310003469644361,3.3145920980761634,3.9968336293737097,3.6153323209604746,2.9057113116909012,1.6073687471255553,37.876362369181457,37.876362369181457,3.0061082958007526,0,0,0.23292329387839425,0.20506543562421634,0.13681552558866916,7.2705198609040761E-2,7.3986086776113495,7.3986086776113495,0.17127672727530663,38.395135175283386,41.369512852091894,8.3315793719906228,23.089615666625118,4.6083861727779265,1.7916934369717314,0.18568386190149916,0.35348997680720962,null,null,9.0231888160550042,0.71613748147551337,-0.76177256073046695,-0.76177256073046684]
[10,3638,9.1625617492548752,8.0765998557625185,9.5648314919901125,9.979127716600777,10.851208024029328,18.485966237078721,13.245331479227206,1.0163726195054135,2.2306631349635171,0.24497136591280944,2.5682504433712361,0.9601336607465405,0.59681644132161482,0.17283688443336842,1.0265688587458013,0.13920565368358886,0.1900000000000126,7.0362667904706244E-2,0.65232885837101529,0.36404376113439951,14.158626314785847,0.97308792194032623,8.0765998557624882E-2,2.7497057930364854,7.5522801341927579,3.7851541024984701,0.6562574785252886,1.4031799496262425,2.6910935805246448,3.6035658818049741,2.3833180351567447,31.059315048680752,3.7810583171640522,0,0,0,0,6.2316785566059352E-2,0.1249811683562301,0.22860580587628077,0.12523997762572484,6.0522888545181424,21.704737009707852,2.6729971114134181,4.0765337467713234,3.6035658818049741,2.6910935805246448,1.4031799496262425,31.059315048680752,31.059315048680752,2.3833180351567447,0,0,0.27189604256424349,0.22860580587628077,0.1249811683562301,6.2316785566059352E-2,6.0522888545181424,6.0522888545181424,0.13546746490995448,31.567837396071564,34.381059205355612,6.0982953163186373,21.321931334989724,5.1765019171174123,1.6124739670714348,0.20173068159760449,0.42655788150330165,null,null,10.676407270110971,0.81924775088093438,-0.6562574785252886,-0.6562574785252886]
[10.5,4188,11.46452979327818,5.8009465298326166,10.356166442847218,10.525463622254309,10.131846841974497,8.8800565265301312,12.191123723578013,1.013071194183601,1.5336410147023123,0.17561460686804131,1.9265729952259909,0.48553079908116781,0.55725157630860034,0.12181460027308702,0.55309176016473738,9.6848837108265612E-2,0.19000000000001813,5.0441455540031155E-2,0.36713696355918785,0.64593423062441102,7.1309778437328459,1.6284484975290234,5.8009465298326186E-2,2.8026530416747573,3.1821780727926523,6.7360774490081461,0.50685916844063561,1.0447203668994824,1.9821081640939926,3.1214591706797084,1.6852871686857884,20.280454622701889,3.3236972521333978,0,0,0,0,4.69335740919294E-2,9.2717451588731958E-2,0.26058451911648861,9.3060939601317699E-2,3.9637496766944595,19.423208642905355,2.5210747787043837,3.6892958707629977,3.1214591706797084,1.9821081640939926,1.0447203668994824,20.280454622701889,20.280454622701889,1.6852871686857884,0,0,0.34179202144507387,0.26058451911648861,9.2717451588731958E-2,4.69335740919294E-2,3.9637496766944595,3.9637496766944595,9.634030210508604E-2,20.545544383206941,22.647731985300972,3.8357500754734186,17.992070253410631,5.3563303080092242,1.2587618693300622,0.22638852165451392,0.49228044806505084,null,null,10.001120257041165,0.83108391578203655,-0.50685916844063561,-0.50685916844063561]
[11,6498,14.650491357622874,3.8059659695426,10.999816611591694,11.007317086350056,11.448576788616871,2.449657205866306,11.138115691246462,1.0119404014939846,1.0023585116979234,0.11776573728930448,0.76352732988576955,0.13276980923735074,0.62967172337392696,8.0862033623800747E-2,0.19470806512360794,5.1584988321533465E-2,0.19000000000003106,3.3825632773707461E-2,0.14252990110249963,0.86941050039148415,2.4185640062473892,2.0270199514854008,3.8059659695426039E-2,2.7783694877679626,0.73370818401952764,10.652040401051499,0.23166969475423585,0.67852881057190151,1.0724944941112859,3.0167930368575528,1.3378019154435252,14.724772806958311,3.2756729496095756,0,0,0,0,3.0976966848491189E-2,5.0097868442563497E-2,0.57086143613526807,5.0792561175828387E-2,2.8808709042763341,16.968818385049545,2.3314877731205916,3.7941295548513736,3.0167930368575528,1.0724944941112859,0.67852881057190151,14.724772806958311,14.724772806958311,1.3378019154435252,0,0,0.88684342257441062,0.57086143613526807,5.0097868442563497E-2,3.0976966848491189E-2,2.8808709042763341,2.8808709042763341,7.7036877090282646E-2,14.9005925061811,15.781885573356174,1.9217711459793174,14.944081660789061,7.75357281087072,1.0560625892968305,0.46335866132132519,0.49932348722923248,null,null,11.313489185444807,1.0278737540510916,-0.23166969475423585,-0.23166969475423593]
[11.5,4710,16.789973827390209,3.4247706833270057,11.507105297118338,11.464763253953073,18.389427178988349,0.40459067932820886,12.366768447843677,1.0105636945103837,1.2566482805263319,0.15075164039067054,0.19949119787819708,2.1922413488157249E-2,1.0114184948443588,0.10268736058526899,0.11885395503818962,3.8418771889360451E-2,0.19000000000002215,4.3300112114629162E-2,7.9090800316816715E-2,0.93147289419356771,0.93476464514169799,2.1828871683235507,3.4247706833270108E-2,2.7723893459872655,7.4720261072530908E-2,18.315101871665771,8.2852058298269082E-2,0.45208107318379437,0.57331707697326006,2.8379929158158186,1.6213343221720149,19.841071124722525,4.5996326858808274,0,0,0,0,2.6996169125577535E-2,3.4452828707937026E-2,1.0288762191091545,3.6596583433420801E-2,3.8867346019852653,11.818879583937441,2.3434790018376304,3.311683837616187,2.8379929158158186,0.57331707697326006,0.45208107318379437,19.841071124722525,19.841071124722525,1.6213343221720149,0,0,1.3900906677942861,1.0288762191091545,3.4452828707937026E-2,2.6996169125577535E-2,3.8867346019852653,3.8867346019852653,9.2587204178622554E-2,20.050666138842889,20.400908977111758,1.5121933914594536,15.791539131170683,13.259326652321576,1.2918885744862392,0.96632952549801976,0.68905626489461647,null,null,18.197197543196911,1.4870034363904345,-8.285205829826911E-2,-8.2852058298269082E-2]
[12,2039,19.667173013185035,3.5490379677952522,12.023363299533328,11.971292819335444,34.377718265300125,7.3331684657678255E-3,13.905546156655928,1.0033271864254041,1.6902484497315271,0.20236732187046633,1.095989311063391E-2,4.1647859855388329E-4,1.8907745045915054,0.13795163921321105,0.13808876761336722,3.7152961755400352E-2,0.18999999999999798,5.8125587904850909E-2,8.1485067231679642E-2,0.92184211919372394,0.94144546609598634,2.2049000952301649,3.5490379677952592E-2,2.7486048502537863,8.4929201475167479E-4,34.282378921214011,4.7056618342176289E-2,0.45461179574490718,0.53136134053577311,2.6307716048485865,2.5943101750253712,35.955668670779673,7.9713788040122564,0,0,0,0,3.3096624034792993E-2,3.8788391300360194E-2,0.89211225367980451,4.2021141112654342E-2,7.0902874480894846,11.553595009245726,2.3918413460633037,2.8384529436141634,2.6307716048485865,0.53136134053577311,0.45461179574490718,35.955668670779673,35.955668670779673,2.5943101750253712,0,0,1.0289738270214475,0.89211225367980451,3.8788391300360194E-2,3.3096624034792993E-2,7.0902874480894846,7.0902874480894846,0.14702425947960618,36.075299883497422,36.288627098478521,1.6013929820964035,17.454584124451181,22.527449718351331,2.0790313214993046,1.6405719662529934,1.1979960268331957,null,null,34.263716492901054,2.4722307112579776,-4.705661834217615E-2,-4.7056618342176358E-2]
[12.5,930,21.72286450114953,3.6942481285607673,12.495069407453366,12.46241424642869,53.288810555729889,0,15.07802534724037,0.99080944503513357,2.0514916316567904,0.24112044661127788,0,0,2.93088458056515,0.16554052960680662,0.16554052960680662,3.7877278724939664E-2,0.18999999999999825,6.9256575545985799E-2,9.6714983402337307E-2,0.89409446163279682,1.1274914963911948,2.1306008557726175,3.6942481285607578E-2,2.7220333801040875,1.7191938883167157E-3,52.960941864841971,3.7070481196692352E-2,0.53903255735382827,0.61448020671058412,2.6718250604662166,3.6702619151330209,55.853628025744484,11.863551676983512,0,0,0,0,3.9216341585562232E-2,4.4805607585629383E-2,0.78330314535167511,4.8498575682762016E-2,11.142458508216942,11.657878197639713,2.3829706448261749,2.8060561086011591,2.6718250604662166,0.61448020671058412,0.53903255735382827,55.853628025744484,55.853628025744484,3.6702619151330209,0,0,0.85515622868565322,0.78330314535167511,4.4805607585629383E-2,3.9216341585562232E-2,11.142458508216942,11.142458508216942,0.20709477537941434,55.340302187386676,55.581422633997953,1.7219037468805358,18.772273475801136,32.139021874854038,2.9608253206862005,2.2943137331072618,1.7237648042954623,null,null,53.783107158249081,3.5342035398211467,-3.7070481196692241E-2,-3.7070481196692227E-2]
[13,464,23.744602722280749,3.7185122805273356,13.060503000260518,12.955257194443107,70.903764712651551,0,16.876794863046502,1.0080202344555247,2.089879607961783,0.24489830916896657,0,0,3.8997070591958352,0.1683277734783972,0.1683277734783972,3.8514699127517163E-2,0.18999999999999878,7.0341683952618361E-2,0.14327814063080707,0.86474209382471734,1.5027537358645879,2.1944802985938594,3.7185122805273314E-2,2.7219756128781207,0,70.573543697625553,2.8630980510882687E-2,0.55567307188792736,0.62304392617920856,2.6776199566588899,4.3250892668275833,72.412876076877922,15.4951949230477,0,0,0,0,4.0384220522616518E-2,4.5373012723744971E-2,0.77454342009385546,4.9102527376015538E-2,14.218177701019618,10.48836709667261,2.5377280859403601,2.7804323507216284,2.6776199566588899,0.62304392617920856,0.55567307188792736,72.412876076877922,72.412876076877922,4.3250892668275833,0,0,0.82712307352060088,0.77454342009385546,4.5373012723744971E-2,4.0384220522616518E-2,14.218177701019618,14.218177701019618,0.24281222005533146,72.993644320613328,73.238542629782287,1.7596585929357731,20.595307143573837,41.481708220929633,3.5560791649875556,2.9489983459354074,2.2423458878807336,null,null,70.339624433183857,4.201257720321216,-2.8630980510882816E-2,-2.8630980510882427E-2]
[13.5,165,25.364987249751529,3.5014753297817323,13.493269665065702,13.469883733833289,84.404571639961588,0,17.614344383816416,1.0113805883612634,1.6321361573481468,0.1976363731554924,0,0,4.6422514401978869,0.13414675656959041,0.13414675656959041,3.5277416506289946E-2,0.19000000000000056,5.676672634131464E-2,0.1118241766558517,0.89955641170541123,1.0697327378128851,1.8146634183367534,3.5014753297817301E-2,2.7828651092756385,0,84.304789918325241,1.8970230255593086E-2,0.47704696021343057,0.51972407890751204,3.0215792506520867,4.8844683584339332,85.068577336168502,19.108596803141452,0,0,0,0,3.524805049826138E-2,3.8456948402053111E-2,1.2097810333401871,4.1700316776709608E-2,16.651973224475118,9.5662026746244457,2.0172869591318343,3.1328562184998954,3.0215792506520867,0.51972407890751204,0.47704696021343057,85.068577336168502,85.068577336168502,4.8844683584339332,0,0,1.2936909594376391,1.2097810333401871,3.8456948402053111E-2,3.524805049826138E-2,16.651973224475118,16.651973224475118,0.27376354084991233,86.036707797309731,86.234344170465221,1.5323544357118648,21.11581971359815,56.146741114330275,4.083873860456011,4.2303685298910727,3.063985237601734,null,null,83.454806836585661,4.7918088689982827,-1.8970230255593055E-2,-1.8970230255593086E-2]
[14,110,27.714326281770138,3.4389979740406766,14.382108836762287,13.969588230639243,92.517715600098882,0,16.713244720239928,0.99439833890105167,1.0495200949013768,0.1288120662381918,0,0,5.0884743580054357,8.6981118813190234E-2,8.6981118813190234E-2,3.7471012642383311E-2,0.19000000000000017,3.6998449206764948E-2,6.3912679109792384E-2,0.9304856597912593,0.58792086109803832,2.1968721303452177,3.4389979740406751E-2,2.8626374647720207,0,92.910142287128934,1.1216747904389117E-2,0.32492572313335327,0.34153051774828014,2.2880198355646577,5.5983884195562146,94.094320188029528,21.134146633299185,0,0,0,0,2.4218924483475558E-2,2.5482218188963804E-2,1.0493634384179718,2.7646727289840859E-2,18.708654164630609,9.1988142147519518,2.3609951504658904,2.3450424445559674,2.2880198355646577,0.34153051774828014,0.32492572313335327,94.094320188029528,94.094320188029528,5.5983884195562146,0,0,1.0981915132067297,1.0493634384179718,2.5482218188963804E-2,2.4218924483475558E-2,18.708654164630609,18.708654164630609,0.31441999965780637,93.567235695000264,93.696047761238461,1.4419467819315157,20.152242694280606,64.889520797477104,4.6494104493804196,4.998424032338348,3.5682386690089207,null,null,93.038887919245539,5.5355927079832012,-1.1216747904389009E-2,-1.1216747904389092E-2]
[14.5,31,27.692086214058929,3.2977589452157168,15.075274781553611,14.374901458249369,99.24062881490353,0,16.454678402065174,0.97574805140482024,0.95903542580153289,0.11806590681451226,0,0,5.4582345848196949,7.963571286584667E-2,7.963571286584667E-2,3.8322779142794618E-2,0.19000000000000011,3.3911849905814348E-2,3.309574158123664E-2,0.9426523098235835,0.48795692818064101,2.1538256201589072,3.2977589452157174E-2,2.868390001811711,0,99.568644477096328,9.5712439065433006E-3,0.31172885287403057,0.32569379877212912,2.9909835570334145,6.0894331564772077,102.69009924892387,23.474333896457924,0,0,0,0,2.33056240185875E-2,2.4374210752346172E-2,1.9360028620449998,2.6443374181238054E-2,20.778400075384432,14.743797989324531,2.2848568848910937,3.0807133663337383,2.9909835570334145,0.32569379877212912,0.31172885287403057,102.69009924892387,102.69009924892387,6.0894331564772077,0,0,2.0498668907539566,1.9360028620449998,2.4374210752346172E-2,2.33056240185875E-2,20.778400075384432,20.778400075384432,0.34222019267255327,100.19966424070506,100.31773014751957,1.2870510879943136,19.752437347280889,77.852126598060707,5.0787519729219266,6.3594569700153825,4.2886486393638048,null,null,101.70722726222529,6.0311497064839727,-9.5712439065432434E-3,-9.5712439065432624E-3]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CELL(\"filename\")","v":"/Users/signhildgehlin/Dropbox/Gehlin-Spitler_collaboration/Studenthuset/studenthuset data detailed excel files/2021_update/20211208_Results/[BinResultsHPEFT_V2.xlsm]Plot (2)"}]

{"sheet":"Plot3","index":3,"n_rows":183,"n_cols":76,"rows_kept":183,"cut":false,"hidden":false,"merged":[]}
[]
["HP EFT / BH ExFT (°C)","Count","ODA Temperature (°C)","EL 007 (kW)","GHE EFT (°C)","GHE ExFT (°C)","Clg Provided (kW)","Bldg Htg Provided (kW)","EL 003 (kW)","CP Energy (kW)","DHW Provided by HP (kW)","DHW by LPS (kW)","Useful Bldg Htg by LPS (kW)","Bldg Htg Uncertainty (kW)","Bldg Clg Uncertainty (kW)","DHW Htg by HP Uncertainty (kW)","Bldg + DHW Htg by HP Uncertainty (kW)","EL007+EL011 Uncertainty (kW)","EL011 Uncertainty (kW)","LPS DHW Uncertainty (kW)","CP Power for Heat Extraction from GHE (kW)","CP Power for Heat Rejection to GHE (kW)","Heat Extraction by GHE (kW)","Heat Rejection to GHE (kW)","EL007 Uncertainty (kW)","LPS Electricity going to bldg heat (kW)","Alt Calc GHE Heat Extraction (kW)","Alt Calc GHE Heat Extraction (kW)","HtgFrac","COP H4","COP H3","COP H2","COP C3","COP C2","Overall (H+C) COP","Not used","Not used","Not used","Not used","Error COP H4","Error COP H3","Error COP H2","Error COP H3b","Error COP C2","BPF0, heating","BPF0, cooling","BPF1*, heating","BPF2, heating","BPF3+, heating","BPF4+, heating","BPFC2","BPFC2","BPFC5*","Error BPF0, heating","Error BPF0, cooling","Error BPF1*, heating","Error BPF2, heating","Error BPF3+, heating","Error BPF4+, heating","Error BPF2, cooling","Error BPF3, cooling","Error BPF4, cooling","Htg & Clg Provided Boundary 2","Htg & Clg Provided Boundary 4+","Electricity Used Boundary 2","Electricity Used Boundary 4+","BPFHC2","BPFHC4+","Error BPFHC2","Error BPFHC4+",null,null,"BPFC2* w/all SSCP power allocated to cooling","BPFC5* w/all LSCPF & SSCP power allocated to cooling","Difference BPF2*","Difference BPF2*"]
[6.5,36,-7.0411861459593581,30.484337959459669,5.2780850062215929,6.6402453190685424,8.0436702536399949,104.75341582045593,14.993770169517253,1.0589186309565459,4.2940337543861498,0.43627920977577606,2.4035603732898521,5.2631852146390337,0.44240186395019976,0.31829755733395204,5.2931230985630497,0.35627645845993844,0.19000000000000014,0.12531166259695264,0.99518451049720036,6.3734120459345595E-2,52.574276917265792,0.43414671121875065,0.30484337959459668,2.5608379621679296,73.388006323535535,0.93036642080595888,0.93130418203000731,2.5172570283410152,3.5553055032715042,3.8298013011981622,7.8093180370692474,110.57612587542329,3.8021108907311207,0,0,0,0,0.12078274552885053,0.17294200809607552,0.19304429275198728,0.17298784204666051,20.751673115392062,52.828672836758038,6.8118412569242563,3.9672053576390969,3.8298013011981622,3.5553055032715042,2.5172570283410152,110.57612587542329,110.57612587542329,7.8093180370692474,0,0,0.20044469583491742,0.19304429275198728,0.17294200809607552,0.12078274552885053,20.751673115392062,20.751673115392062,0.44076511874953817,117.09111982848208,119.9309594115477,28.546139418472507,45.47810812897692,4.1018197981864821,2.6371140829214101,0.18725152918687613,0.20166772099798613,null,null,{"$f":"G3/J3","v":7.5961174149650761},{"$f":"G3/(I3)","v":0.53646749034428964},{"$f":"(BU3-AY3)/AY3","v":-0.93130418203000731},{"$f":"(BV3-BA3)/BA3","v":-0.93130418203000731}]
[7,271,-6.5215819137791078,27.573372148678338,5.3323478659701884,7.0662003087664926,7.5550134740443395,89.50567159290307,14.02168824167614,1.0647245464717638,3.121082755977334,0.31744130618210653,2.6063791678716934,4.4959644291915088,0.41552574107243867,0.23146982925756227,4.5108365176366902,0.32786125813451489,0.18999999999999947,9.1178073498098491E-2,1.0155488452051573,4.9175701266606975E-2,60.31582591058239,9.2337358929828514E-2,0.2757337214867831,2.6698502606884253,59.97888031224506,0.5579445656885017,0.92458694193340529,2.3570827040473743,3.345865796869167,3.6224052921654954,7.1447721626814022,94.091723680930116,3.6002947191123775,0,0,0,0,0.11289643986997469,0.16255825722836023,0.18337879295982334,0.16258960815219256,17.57006945846172,59.392343554285283,1.8777029417276596,3.7674469519724316,3.6224052921654954,3.345865796869167,2.3570827040473743,94.091723680930116,94.091723680930116,7.1447721626814022,0,0,0.19126250100203224,0.18337879295982334,0.16255825722836023,0.11289643986997469,17.57006945846172,17.57006945846172,0.40471299002918831,100.18176782292474,103.10558829697854,25.650805128279572,41.595060390354476,3.9055993494908301,2.4787940522112528,0.17793880666221265,0.20016022613252341,null,null,{"$f":"G4/J4","v":7.0957446215359665},{"$f":"G4/(I4)","v":0.53880911797688213},{"$f":"(BU4-AY4)/AY4","v":-0.92458694193340529},{"$f":"(BV4-BA4)/BA4","v":-0.92458694193340529}]
[7.5,1041,-3.6273399084647271,22.303652351738521,6.1154874257299721,7.5505014614738633,7.0268158392849003,69.555186852758169,12.987059083453744,1.0173398289775222,2.1037282465901885,0.21395119728546155,2.7780209203683399,3.505530250084929,0.38647487116067042,0.15601290764450551,3.5211063789260169,0.28234549224996397,0.1899999999999982,6.1452802805407512E-2,0.94284627267708898,7.4493556300432404E-2,46.534465672831175,0.150903995833473,0.22303652351738509,2.7843204485575166,44.931870863455089,0.62249213826467975,0.91069771157409618,2.1871912416376822,3.2135356351340008,3.5418829771673956,6.0587797770846734,77.344588993155313,3.5023253909336569,0,0,0,0,0.10473927632490038,0.15652633272455019,0.18211132280670111,0.15654868549043538,15.058355867336132,49.355305335940535,2.0257322019219677,3.7118623139850806,3.5418829771673956,3.2135356351340008,2.1871912416376822,77.344588993155313,77.344588993155313,6.0587797770846734,0,0,0.19163348841826727,0.18211132280670111,0.15652633272455019,0.10473927632490038,15.058355867336132,15.058355867336132,0.34482044907702647,78.685730938633256,81.677703056287058,20.322720534873067,35.290711435192264,3.871810902659973,2.3144249502104737,0.17545458270629355,0.21505965603755475,null,null,6.9070487944497412,0.54106289916224881,-0.91069771157409629,-0.91069771157409618]
[8,2951,0.71646430629359581,18.838658405575497,6.7897360586838165,8.0389630307381736,8.5594676452811207,56.899907175400621,13.329631324385328,0.98428148039573959,2.0234208992252007,0.20593269951882195,2.7894102974310733,2.872027469464502,0.4707707204904637,0.15012025069236817,2.8892086945585618,0.25107135743355719,0.19000000000000283,5.9149664667827923E-2,0.9292558670506269,5.502561334511219E-2,39.759367537750109,0.15821245017054544,0.18838658405575526,2.7940130217421184,34.25461462466771,0.71374836003336084,0.87316074335734517,2.0316144854695111,3.1433838196076,3.5287341949233597,5.0626153175334538,68.56046472882413,3.5553827596851288,0,0,0,0,9.6263900445057934E-2,0.15204821617232761,0.18296969115640341,0.15207786465563247,13.761232512828682,42.786243216244308,2.8752510068040729,3.7202094165758148,3.5287341949233597,3.1433838196076,2.0316144854695111,68.56046472882413,68.56046472882413,5.0626153175334538,0,0,0.19399149053892095,0.18296969115640341,0.15204821617232761,9.6263900445057934E-2,13.761232512828682,13.761232512828682,0.28764278463380499,67.482795719906946,70.478138716856847,16.822994164710298,32.168289729960826,4.0113427526157048,2.1909196699137872,0.17538878805268146,0.2316952276615698,null,null,8.6961583812790089,0.64213836354366127,-0.87316074335734517,-0.87316074335734517]
[8.5,7336,2.7765456079707138,15.913120472779555,7.4450098467727468,8.5212861987749875,8.2870194435506139,47.29654335425468,13.279647924181813,0.99201476031052882,1.9164731535499375,0.19739489832334342,2.799357362218271,2.389920521669386,0.45578606939528615,0.14313889921090869,2.407998368577565,0.22820801682597325,0.19000000000003375,5.6697367976272665E-2,0.93979805867604871,5.2216701634482839E-2,34.15185142219886,0.16373065411075791,0.15913120472779585,2.8023481914232269,27.531138023565791,0.51053310265523677,0.85587801283182863,1.913926466066372,3.1147391514542853,3.5758982006643563,4.3299367784178626,57.962883468947688,3.5786042156871081,0,0,0,0,8.9713720833684285E-2,0.14978483496708578,0.1877717906647775,0.14982302169292916,11.550261071759074,36.339563704047947,3.1355993194835108,3.8110104775893943,3.5758982006643563,3.1147391514542853,1.913926466066372,57.962883468947688,57.962883468947688,4.3299367784178626,0,0,0.2018454905540478,0.1877717906647775,0.14978483496708578,8.9713720833684285E-2,11.550261071759074,11.550261071759074,0.24607254534903178,57.50003595135523,60.496788211896842,13.905392143343514,29.19276839696137,4.13508913366966,2.0723210416109032,0.1780108920089026,0.25574870768312236,null,null,8.353725947541891,0.62403909281813241,-0.85587801283182863,-0.85587801283182863]
[9,7811,4.6981658913645505,12.992645680866216,8.0779247074422305,8.9778785506672332,8.580242496449376,38.743664306428236,12.984636102037753,1.0081271408660961,1.8195317844766028,0.18976355788131116,2.8067875081455855,1.9603347226161669,0.47191333730471369,0.13685550791942569,1.9820156316513238,0.203490205908957,0.190000000000035,5.4505432313957207E-2,0.96669088243971613,4.1436258426381004E-2,28.78725090863065,0.16609825115849114,0.12992645680866238,2.8099868633055038,21.451575683831912,0.46964448992200764,0.82540410799301944,1.8371719644691136,3.1508506166520664,3.7471748568572294,3.7847374544167507,48.747262716421254,3.7240794002776942,0,0,0,0,8.5067327095352682E-2,0.15068200094458914,0.20179519273445912,0.15073357114490146,9.5705287428405086,29.779168741074635,4.0085243568406321,4.0592035678162626,3.7471748568572294,3.1508506166520664,1.8371719644691136,48.747262716421254,48.747262716421254,3.7847374544167507,0,0,0.22184592974809866,0.20179519273445912,0.15068200094458914,8.5067327095352682E-2,9.5705287428405086,9.5705287428405086,0.21540161722654844,49.143438587354218,52.139989653381114,11.001022400545496,25.977281782903969,4.4671701227439913,2.0071380096317548,0.18779443100271459,0.2984486476124823,null,null,8.5110718168721942,0.66079961186612157,-0.82540410799301944,-0.82540410799301944]
[9.5,4714,6.6557330133081303,10.317243084799726,8.8555962676717765,9.4789220240066321,9.1467747332153362,27.428028693531129,12.772372581825392,1.0136964791139509,1.8203317485369239,0.19529293973080417,2.779084737077703,1.396167471403676,0.5030726103268448,0.13914499077775166,1.4303999195286647,0.17408630208878376,0.19000000000002218,5.6093626335508982E-2,0.84955991959931831,0.16413655951463041,20.652804593130213,0.5440457431726019,0.10317243084799695,2.8040672521922496,13.22066337958735,1.4506570427251839,0.76177256073046695,1.6073687471255553,2.9057113116909012,3.6153323209604746,3.0061082958007526,37.876362369181457,3.6510222844929707,0,0,0,0,7.2705198609040761E-2,0.13681552558866916,0.20506543562421634,0.13690900013522078,7.3986086776113495,24.310003469644361,3.3145920980761634,3.9968336293737097,3.6153323209604746,2.9057113116909012,1.6073687471255553,37.876362369181457,37.876362369181457,3.0061082958007526,0,0,0.23292329387839425,0.20506543562421634,0.13681552558866916,7.2705198609040761E-2,7.3986086776113495,7.3986086776113495,0.17127672727530663,38.395135175283386,41.369512852091894,8.3315793719906228,23.089615666625118,4.6083861727779265,1.7916934369717314,0.18568386190149916,0.35348997680720962,null,null,9.0231888160550042,0.71613748147551337,-0.76177256073046695,-0.76177256073046684]
[10,3638,9.1625617492548752,8.0765998557625185,9.5648314919901125,9.979127716600777,10.851208024029328,18.485966237078721,13.245331479227206,1.0163726195054135,2.2306631349635171,0.24497136591280944,2.5682504433712361,0.9601336607465405,0.59681644132161482,0.17283688443336842,1.0265688587458013,0.13920565368358886,0.1900000000000126,7.0362667904706244E-2,0.65232885837101529,0.36404376113439951,14.158626314785847,0.97308792194032623,8.0765998557624882E-2,2.7497057930364854,7.5522801341927579,3.7851541024984701,0.6562574785252886,1.4031799496262425,2.6910935805246448,3.6035658818049741,2.3833180351567447,31.059315048680752,3.7810583171640522,0,0,0,0,6.2316785566059352E-2,0.1249811683562301,0.22860580587628077,0.12523997762572484,6.0522888545181424,21.704737009707852,2.6729971114134181,4.0765337467713234,3.6035658818049741,2.6910935805246448,1.4031799496262425,31.059315048680752,31.059315048680752,2.3833180351567447,0,0,0.27189604256424349,0.22860580587628077,0.1249811683562301,6.2316785566059352E-2,6.0522888545181424,6.0522888545181424,0.13546746490995448,31.567837396071564,34.381059205355612,6.0982953163186373,21.321931334989724,5.1765019171174123,1.6124739670714348,0.20173068159760449,0.42655788150330165,null,null,10.676407270110971,0.81924775088093438,-0.6562574785252886,-0.6562574785252886]
[10.5,4188,11.46452979327818,5.8009465298326166,10.356166442847218,10.525463622254309,10.131846841974497,8.8800565265301312,12.191123723578013,1.013071194183601,1.5336410147023123,0.17561460686804131,1.9265729952259909,0.48553079908116781,0.55725157630860034,0.12181460027308702,0.55309176016473738,9.6848837108265612E-2,0.19000000000001813,5.0441455540031155E-2,0.36713696355918785,0.64593423062441102,7.1309778437328459,1.6284484975290234,5.8009465298326186E-2,2.8026530416747573,3.1821780727926523,6.7360774490081461,0.50685916844063561,1.0447203668994824,1.9821081640939926,3.1214591706797084,1.6852871686857884,20.280454622701889,3.3236972521333978,0,0,0,0,4.69335740919294E-2,9.2717451588731958E-2,0.26058451911648861,9.3060939601317699E-2,3.9637496766944595,19.423208642905355,2.5210747787043837,3.6892958707629977,3.1214591706797084,1.9821081640939926,1.0447203668994824,20.280454622701889,20.280454622701889,1.6852871686857884,0,0,0.34179202144507387,0.26058451911648861,9.2717451588731958E-2,4.69335740919294E-2,3.9637496766944595,3.9637496766944595,9.634030210508604E-2,20.545544383206941,22.647731985300972,3.8357500754734186,17.992070253410631,5.3563303080092242,1.2587618693300622,0.22638852165451392,0.49228044806505084,null,null,10.001120257041165,0.83108391578203655,-0.50685916844063561,-0.50685916844063561]
[11,6498,14.650491357622874,3.8059659695426,10.999816611591694,11.007317086350056,11.448576788616871,2.449657205866306,11.138115691246462,1.0119404014939846,1.0023585116979234,0.11776573728930448,0.76352732988576955,0.13276980923735074,0.62967172337392696,8.0862033623800747E-2,0.19470806512360794,5.1584988321533465E-2,0.19000000000003106,3.3825632773707461E-2,0.14252990110249963,0.86941050039148415,2.4185640062473892,2.0270199514854008,3.8059659695426039E-2,2.7783694877679626,0.73370818401952764,10.652040401051499,0.23166969475423585,0.67852881057190151,1.0724944941112859,3.0167930368575528,1.3378019154435252,14.724772806958311,3.2756729496095756,0,0,0,0,3.0976966848491189E-2,5.0097868442563497E-2,0.57086143613526807,5.0792561175828387E-2,2.8808709042763341,16.968818385049545,2.3314877731205916,3.7941295548513736,3.0167930368575528,1.0724944941112859,0.67852881057190151,14.724772806958311,14.724772806958311,1.3378019154435252,0,0,0.88684342257441062,0.57086143613526807,5.0097868442563497E-2,3.0976966848491189E-2,2.8808709042763341,2.8808709042763341,7.7036877090282646E-2,14.9005925061811,15.781885573356174,1.9217711459793174,14.944081660789061,7.75357281087072,1.0560625892968305,0.46335866132132519,0.49932348722923248,null,null,11.313489185444807,1.0278737540510916,-0.23166969475423585,-0.23166969475423593]
[11.5,4710,16.789973827390209,3.4247706833270057,11.507105297118338,11.464763253953073,18.389427178988349,0.40459067932820886,12.366768447843677,1.0105636945103837,1.2566482805263319,0.15075164039067054,0.19949119787819708,2.1922413488157249E-2,1.0114184948443588,0.10268736058526899,0.11885395503818962,3.8418771889360451E-2,0.19000000000002215,4.3300112114629162E-2,7.9090800316816715E-2,0.93147289419356771,0.93476464514169799,2.1828871683235507,3.4247706833270108E-2,2.7723893459872655,7.4720261072530908E-2,18.315101871665771,8.2852058298269082E-2,0.45208107318379437,0.57331707697326006,2.8379929158158186,1.6213343221720149,19.841071124722525,4.5996326858808274,0,0,0,0,2.6996169125577535E-2,3.4452828707937026E-2,1.0288762191091545,3.6596583433420801E-2,3.8867346019852653,11.818879583937441,2.3434790018376304,3.311683837616187,2.8379929158158186,0.57331707697326006,0.45208107318379437,19.841071124722525,19.841071124722525,1.6213343221720149,0,0,1.3900906677942861,1.0288762191091545,3.4452828707937026E-2,2.6996169125577535E-2,3.8867346019852653,3.8867346019852653,9.2587204178622554E-2,20.050666138842889,20.400908977111758,1.5121933914594536,15.791539131170683,13.259326652321576,1.2918885744862392,0.96632952549801976,0.68905626489461647,null,null,18.197197543196911,1.4870034363904345,-8.285205829826911E-2,-8.2852058298269082E-2]
[12,2039,19.667173013185035,3.5490379677952522,12.023363299533328,11.971292819335444,34.377718265300125,7.3331684657678255E-3,13.905546156655928,1.0033271864254041,1.6902484497315271,0.20236732187046633,1.095989311063391E-2,4.1647859855388329E-4,1.8907745045915054,0.13795163921321105,0.13808876761336722,3.7152961755400352E-2,0.18999999999999798,5.8125587904850909E-2,8.1485067231679642E-2,0.92184211919372394,0.94144546609598634,2.2049000952301649,3.5490379677952592E-2,2.7486048502537863,8.4929201475167479E-4,34.282378921214011,4.7056618342176289E-2,0.45461179574490718,0.53136134053577311,2.6307716048485865,2.5943101750253712,35.955668670779673,7.9713788040122564,0,0,0,0,3.3096624034792993E-2,3.8788391300360194E-2,0.89211225367980451,4.2021141112654342E-2,7.0902874480894846,11.553595009245726,2.3918413460633037,2.8384529436141634,2.6307716048485865,0.53136134053577311,0.45461179574490718,35.955668670779673,35.955668670779673,2.5943101750253712,0,0,1.0289738270214475,0.89211225367980451,3.8788391300360194E-2,3.3096624034792993E-2,7.0902874480894846,7.0902874480894846,0.14702425947960618,36.075299883497422,36.288627098478521,1.6013929820964035,17.454584124451181,22.527449718351331,2.0790313214993046,1.6405719662529934,1.1979960268331957,null,null,34.263716492901054,2.4722307112579776,-4.705661834217615E-2,-4.7056618342176358E-2]
[12.5,930,21.72286450114953,3.6942481285607673,12.495069407453366,12.46241424642869,53.288810555729889,0,15.07802534724037,0.99080944503513357,2.0514916316567904,0.24112044661127788,0,0,2.93088458056515,0.16554052960680662,0.16554052960680662,3.7877278724939664E-2,0.18999999999999825,6.9256575545985799E-2,9.6714983402337307E-2,0.89409446163279682,1.1274914963911948,2.1306008557726175,3.6942481285607578E-2,2.7220333801040875,1.7191938883167157E-3,52.960941864841971,3.7070481196692352E-2,0.53903255735382827,0.61448020671058412,2.6718250604662166,3.6702619151330209,55.853628025744484,11.863551676983512,0,0,0,0,3.9216341585562232E-2,4.4805607585629383E-2,0.78330314535167511,4.8498575682762016E-2,11.142458508216942,11.657878197639713,2.3829706448261749,2.8060561086011591,2.6718250604662166,0.61448020671058412,0.53903255735382827,55.853628025744484,55.853628025744484,3.6702619151330209,0,0,0.85515622868565322,0.78330314535167511,4.4805607585629383E-2,3.9216341585562232E-2,11.142458508216942,11.142458508216942,0.20709477537941434,55.340302187386676,55.581422633997953,1.7219037468805358,18.772273475801136,32.139021874854038,2.9608253206862005,2.2943137331072618,1.7237648042954623,null,null,53.783107158249081,3.5342035398211467,-3.7070481196692241E-2,-3.7070481196692227E-2]
[13,464,23.744602722280749,3.7185122805273356,13.060503000260518,12.955257194443107,70.903764712651551,0,16.876794863046502,1.0080202344555247,2.089879607961783,0.24489830916896657,0,0,3.8997070591958352,0.1683277734783972,0.1683277734783972,3.8514699127517163E-2,0.18999999999999878,7.0341683952618361E-2,0.14327814063080707,0.86474209382471734,1.5027537358645879,2.1944802985938594,3.7185122805273314E-2,2.7219756128781207,0,70.573543697625553,2.8630980510882687E-2,0.55567307188792736,0.62304392617920856,2.6776199566588899,4.3250892668275833,72.412876076877922,15.4951949230477,0,0,0,0,4.0384220522616518E-2,4.5373012723744971E-2,0.77454342009385546,4.9102527376015538E-2,14.218177701019618,10.48836709667261,2.5377280859403601,2.7804323507216284,2.6776199566588899,0.62304392617920856,0.55567307188792736,72.412876076877922,72.412876076877922,4.3250892668275833,0,0,0.82712307352060088,0.77454342009385546,4.5373012723744971E-2,4.0384220522616518E-2,14.218177701019618,14.218177701019618,0.24281222005533146,72.993644320613328,73.238542629782287,1.7596585929357731,20.595307143573837,41.481708220929633,3.5560791649875556,2.9489983459354074,2.2423458878807336,null,null,70.339624433183857,4.201257720321216,-2.8630980510882816E-2,-2.8630980510882427E-2]
[13.5,165,25.364987249751529,3.5014753297817323,13.493269665065702,13.469883733833289,84.404571639961588,0,17.614344383816416,1.0113805883612634,1.6321361573481468,0.1976363731554924,0,0,4.6422514401978869,0.13414675656959041,0.13414675656959041,3.5277416506289946E-2,0.19000000000000056,5.676672634131464E-2,0.1118241766558517,0.89955641170541123,1.0697327378128851,1.8146634183367534,3.5014753297817301E-2,2.7828651092756385,0,84.304789918325241,1.8970230255593086E-2,0.47704696021343057,0.51972407890751204,3.0215792506520867,4.8844683584339332,85.068577336168502,19.108596803141452,0,0,0,0,3.524805049826138E-2,3.8456948402053111E-2,1.2097810333401871,4.1700316776709608E-2,16.651973224475118,9.5662026746244457,2.0172869591318343,3.1328562184998954,3.0215792506520867,0.51972407890751204,0.47704696021343057,85.068577336168502,85.068577336168502,4.8844683584339332,0,0,1.2936909594376391,1.2097810333401871,3.8456948402053111E-2,3.524805049826138E-2,16.651973224475118,16.651973224475118,0.27376354084991233,86.036707797309731,86.234344170465221,1.5323544357118648,21.11581971359815,56.146741114330275,4.083873860456011,4.2303685298910727,3.063985237601734,null,null,83.454806836585661,4.7918088689982827,-1.8970230255593055E-2,-1.8970230255593086E-2]
[14,110,27.714326281770138,3.4389979740406766,14.382108836762287,13.969588230639243,92.517715600098882,0,16.713244720239928,0.99439833890105167,1.0495200949013768,0.1288120662381918,0,0,5.0884743580054357,8.6981118813190234E-2,8.6981118813190234E-2,3.7471012642383311E-2,0.19000000000000017,3.6998449206764948E-2,6.3912679109792384E-2,0.9304856597912593,0.58792086109803832,2.1968721303452177,3.4389979740406751E-2,2.8626374647720207,0,92.910142287128934,1.1216747904389117E-2,0.32492572313335327,0.34153051774828014,2.2880198355646577,5.5983884195562146,94.094320188029528,21.134146633299185,0,0,0,0,2.4218924483475558E-2,2.5482218188963804E-2,1.0493634384179718,2.7646727289840859E-2,18.708654164630609,9.1988142147519518,2.3609951504658904,2.3450424445559674,2.2880198355646577,0.34153051774828014,0.32492572313335327,94.094320188029528,94.094320188029528,5.5983884195562146,0,0,1.0981915132067297,1.0493634384179718,2.5482218188963804E-2,2.4218924483475558E-2,18.708654164630609,18.708654164630609,0.31441999965780637,93.567235695000264,93.696047761238461,1.4419467819315157,20.152242694280606,64.889520797477104,4.6494104493804196,4.998424032338348,3.5682386690089207,null,null,93.038887919245539,5.5355927079832012,-1.1216747904389009E-2,-1.1216747904389092E-2]
[14.5,31,27.692086214058929,3.2977589452157168,15.075274781553611,14.374901458249369,99.24062881490353,0,16.454678402065174,0.97574805140482024,0.95903542580153289,0.11806590681451226,0,0,5.4582345848196949,7.963571286584667E-2,7.963571286584667E-2,3.8322779142794618E-2,0.19000000000000011,3.3911849905814348E-2,3.309574158123664E-2,0.9426523098235835,0.48795692818064101,2.1538256201589072,3.2977589452157174E-2,2.868390001811711,0,99.568644477096328,9.5712439065433006E-3,0.31172885287403057,0.32569379877212912,2.9909835570334145,6.0894331564772077,102.69009924892387,23.474333896457924,0,0,0,0,2.33056240185875E-2,2.4374210752346172E-2,1.9360028620449998,2.6443374181238054E-2,20.778400075384432,14.743797989324531,2.2848568848910937,3.0807133663337383,2.9909835570334145,0.32569379877212912,0.31172885287403057,102.69009924892387,102.69009924892387,6.0894331564772077,0,0,2.0498668907539566,1.9360028620449998,2.4374210752346172E-2,2.33056240185875E-2,20.778400075384432,20.778400075384432,0.34222019267255327,100.19966424070506,100.31773014751957,1.2870510879943136,19.752437347280889,77.852126598060707,5.0787519729219266,6.3594569700153825,4.2886486393638048,null,null,101.70722726222529,6.0311497064839727,-9.5712439065432434E-3,-9.5712439065432624E-3]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CELL(\"filename\")","v":"/Users/signhildgehlin/Dropbox/Gehlin-Spitler_collaboration/Studenthuset/studenthuset data detailed excel files/2021_update/20211208_Results/[BinResultsHPEFT_V2.xlsm]Plot (2)"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["HP EFT / BH ExFT (°C)","Number of hours"]
[6.5,36,null,6.45,0]
[7,271,null,6.45,36]
[7.5,1041,null,6.55,36]
[8,2951,null,6.55,0]
[8.5,7336]
[9,7811,null,6.95,0]
[9.5,4714,null,6.95,271]
[10,3638,null,7.05,271]
[10.5,4188,null,7.05,0]
[11,6498]
[11.5,4710,null,7.45,0]
[12,2039,null,7.45,1041]
[12.5,930,null,7.55,1041]
[13,464,null,7.55,0]
[13.5,165,null,null,null,null,null,null,null,null,null,null,{"$f":"CELL(\"filename\")","v":"/Users/signhildgehlin/Dropbox/Gehlin-Spitler_collaboration/Studenthuset/studenthuset data detailed excel files/2021_update/20211208_Results/[BinResultsHPEFT_V2.xlsm]Plot (2)"}]
[14,110,null,7.95,0]
[14.5,31,null,7.95,2951]
[null,null,null,8.0500000000000007,2951]
[null,null,null,8.0500000000000007,0]
[]
[null,null,null,8.4499999999999993,0]
[null,null,null,8.4499999999999993,7336]
[null,null,null,8.5500000000000007,7336]
[null,null,null,8.5500000000000007,0]
[]
[null,null,null,8.9499999999999993,0]
[null,null,null,8.9499999999999993,7811]
[null,null,null,9.0500000000000007,7811]
[null,null,null,9.0500000000000007,0]
[]
[null,null,null,9.4499999999999993,0]
[null,null,null,9.4499999999999993,4714]
[null,null,null,9.5500000000000007,4714]
[null,null,null,9.5500000000000007,0]
[]
[null,null,null,9.9499999999999993,0]
[null,null,null,9.9499999999999993,3638]
[null,null,null,10.050000000000001,3638]
[null,null,null,10.050000000000001,0]
[]
[null,null,null,10.45,0]
[null,null,null,10.45,4188]
[null,null,null,10.55,4188]
[null,null,null,10.55,0]
[]
[null,null,null,10.95,0]
[null,null,null,10.95,6498]
[null,null,null,11.05,6498]
[null,null,null,11.05,0]
[]
[null,null,null,11.45,0]
[null,null,null,11.45,4710]
[null,null,null,11.55,4710]
[null,null,null,11.55,0]
[]
[null,null,null,11.95,0]
[null,null,null,11.95,2039]
[null,null,null,12.05,2039]
[null,null,null,12.05,0]
[]
[null,null,null,12.45,0]
[null,null,null,12.45,930]
[null,null,null,12.55,930]
[null,null,null,12.55,0]
[]
[null,null,null,12.95,0]
[null,null,null,12.95,464]
[null,null,null,13.05,464]
[null,null,null,13.05,0]
[]
[null,null,null,13.45,0]
[null,null,null,13.45,165]
[null,null,null,13.55,165]
[null,null,null,13.55,0]
[]
[null,null,null,13.95,0]
[null,null,null,13.95,110]
[null,null,null,14.05,110]
[null,null,null,14.05,0]
[]
[null,null,null,14.45,0]
[null,null,null,14.45,31]
[null,null,null,14.55,31]
[null,null,null,14.55,0]

{"sheet":"Plot4","index":4,"n_rows":183,"n_cols":76,"rows_kept":183,"cut":false,"hidden":false,"merged":[]}
[]
["HP EFT / BH ExFT (°C)","Count","ODA Temperature (°C)","EL 007 (kW)","GHE EFT (°C)","GHE ExFT (°C)","Clg Provided (kW)","Bldg Htg Provided (kW)","EL 003 (kW)","CP Energy (kW)","DHW Provided by HP (kW)","DHW by LPS (kW)","Useful Bldg Htg by LPS (kW)","Bldg Htg Uncertainty (kW)","Bldg Clg Uncertainty (kW)","DHW Htg by HP Uncertainty (kW)","Bldg + DHW Htg by HP Uncertainty (kW)","EL007+EL011 Uncertainty (kW)","EL011 Uncertainty (kW)","LPS DHW Uncertainty (kW)","CP Power for Heat Extraction from GHE (kW)","CP Power for Heat Rejection to GHE (kW)","Heat Extraction by GHE (kW)","Heat Rejection to GHE (kW)","EL007 Uncertainty (kW)","LPS Electricity going to bldg heat (kW)","Alt Calc GHE Heat Extraction (kW)","Alt Calc GHE Heat Extraction (kW)","HtgFrac","COP H4","COP H3","COP H2","COP C3","COP C2","Overall (H+C) COP","Not used","Not used","Not used","Not used","Error COP H4","Error COP H3","Error COP H2","Error COP H3b","Error COP C2","BPF0, heating","BPF0, cooling","BPFH1*","BPFH2","BPFH3+","BPFH5+*","BPF2, cooling","BPF3, cooling","BPF4, cooling","Error BPF0, heating","Error BPF0, cooling","Error BPF1*, heating","Error BPF2, heating","Error BPF3+, heating","Error BPF4+, heating","Error BPF2, cooling","Error BPF3, cooling","Error BPF4, cooling","Htg & Clg Provided Boundary 2","Htg & Clg Provided Boundary 4+","Electricity Used Boundary 2","Electricity Used Boundary 4+","BPFHC2","BPFHC4+","Error BPFHC2","Error BPFHC4+",null,null,"BPF2* w/all CP power allocated to cooling","BPF4* w/all pumping power allocated to cooling","Difference BPF2*","Difference BPF2*"]
[6.5,36,-7.0411861459593581,30.484337959459669,5.2780850062215929,6.6402453190685424,8.0436702536399949,104.75341582045593,14.993770169517253,1.0589186309565459,4.2940337543861498,0.43627920977577606,2.4035603732898521,5.2631852146390337,0.44240186395019976,0.31829755733395204,5.2931230985630497,0.35627645845993844,0.19000000000000014,0.12531166259695264,0.99518451049720036,6.3734120459345595E-2,52.574276917265792,0.43414671121875065,0.30484337959459668,2.5608379621679296,73.388006323535535,0.93036642080595888,0.93130418203000731,2.5172570283410152,3.5553055032715042,3.8298013011981622,7.8093180370692474,110.57612587542329,3.8021108907311207,0,0,0,0,0.12078274552885053,0.17294200809607552,0.19304429275198728,0.17298784204666051,20.751673115392062,52.828672836758038,6.8118412569242563,3.9672053576390969,3.8298013011981622,3.5553055032715042,2.5172570283410152,110.57612587542329,110.57612587542329,7.8093180370692474,0,0,0.20044469583491742,0.19304429275198728,0.17294200809607552,0.12078274552885053,20.751673115392062,20.751673115392062,0.44076511874953817,117.09111982848208,119.9309594115477,28.546139418472507,45.47810812897692,4.1018197981864821,2.6371140829214101,0.18725152918687613,0.20166772099798613,null,null,{"$f":"G3/J3","v":7.5961174149650761},{"$f":"G3/(I3)","v":0.53646749034428964},{"$f":"(BU3-AY3)/AY3","v":-0.93130418203000731},{"$f":"(BV3-BA3)/BA3","v":-0.93130418203000731}]
[7,271,-6.5215819137791078,27.573372148678338,5.3323478659701884,7.0662003087664926,7.5550134740443395,89.50567159290307,14.02168824167614,1.0647245464717638,3.121082755977334,0.31744130618210653,2.6063791678716934,4.4959644291915088,0.41552574107243867,0.23146982925756227,4.5108365176366902,0.32786125813451489,0.18999999999999947,9.1178073498098491E-2,1.0155488452051573,4.9175701266606975E-2,60.31582591058239,9.2337358929828514E-2,0.2757337214867831,2.6698502606884253,59.97888031224506,0.5579445656885017,0.92458694193340529,2.3570827040473743,3.345865796869167,3.6224052921654954,7.1447721626814022,94.091723680930116,3.6002947191123775,0,0,0,0,0.11289643986997469,0.16255825722836023,0.18337879295982334,0.16258960815219256,17.57006945846172,59.392343554285283,1.8777029417276596,3.7674469519724316,3.6224052921654954,3.345865796869167,2.3570827040473743,94.091723680930116,94.091723680930116,7.1447721626814022,0,0,0.19126250100203224,0.18337879295982334,0.16255825722836023,0.11289643986997469,17.57006945846172,17.57006945846172,0.40471299002918831,100.18176782292474,103.10558829697854,25.650805128279572,41.595060390354476,3.9055993494908301,2.4787940522112528,0.17793880666221265,0.20016022613252341,null,null,{"$f":"G4/J4","v":7.0957446215359665},{"$f":"G4/(I4)","v":0.53880911797688213},{"$f":"(BU4-AY4)/AY4","v":-0.92458694193340529},{"$f":"(BV4-BA4)/BA4","v":-0.92458694193340529}]
[7.5,1041,-3.6273399084647271,22.303652351738521,6.1154874257299721,7.5505014614738633,7.0268158392849003,69.555186852758169,12.987059083453744,1.0173398289775222,2.1037282465901885,0.21395119728546155,2.7780209203683399,3.505530250084929,0.38647487116067042,0.15601290764450551,3.5211063789260169,0.28234549224996397,0.1899999999999982,6.1452802805407512E-2,0.94284627267708898,7.4493556300432404E-2,46.534465672831175,0.150903995833473,0.22303652351738509,2.7843204485575166,44.931870863455089,0.62249213826467975,0.91069771157409618,2.1871912416376822,3.2135356351340008,3.5418829771673956,6.0587797770846734,77.344588993155313,3.5023253909336569,0,0,0,0,0.10473927632490038,0.15652633272455019,0.18211132280670111,0.15654868549043538,15.058355867336132,49.355305335940535,2.0257322019219677,3.7118623139850806,3.5418829771673956,3.2135356351340008,2.1871912416376822,77.344588993155313,77.344588993155313,6.0587797770846734,0,0,0.19163348841826727,0.18211132280670111,0.15652633272455019,0.10473927632490038,15.058355867336132,15.058355867336132,0.34482044907702647,78.685730938633256,81.677703056287058,20.322720534873067,35.290711435192264,3.871810902659973,2.3144249502104737,0.17545458270629355,0.21505965603755475,null,null,6.9070487944497412,0.54106289916224881,-0.91069771157409629,-0.91069771157409618]
[8,2951,0.71646430629359581,18.838658405575497,6.7897360586838165,8.0389630307381736,8.5594676452811207,56.899907175400621,13.329631324385328,0.98428148039573959,2.0234208992252007,0.20593269951882195,2.7894102974310733,2.872027469464502,0.4707707204904637,0.15012025069236817,2.8892086945585618,0.25107135743355719,0.19000000000000283,5.9149664667827923E-2,0.9292558670506269,5.502561334511219E-2,39.759367537750109,0.15821245017054544,0.18838658405575526,2.7940130217421184,34.25461462466771,0.71374836003336084,0.87316074335734517,2.0316144854695111,3.1433838196076,3.5287341949233597,5.0626153175334538,68.56046472882413,3.5553827596851288,0,0,0,0,9.6263900445057934E-2,0.15204821617232761,0.18296969115640341,0.15207786465563247,13.761232512828682,42.786243216244308,2.8752510068040729,3.7202094165758148,3.5287341949233597,3.1433838196076,2.0316144854695111,68.56046472882413,68.56046472882413,5.0626153175334538,0,0,0.19399149053892095,0.18296969115640341,0.15204821617232761,9.6263900445057934E-2,13.761232512828682,13.761232512828682,0.28764278463380499,67.482795719906946,70.478138716856847,16.822994164710298,32.168289729960826,4.0113427526157048,2.1909196699137872,0.17538878805268146,0.2316952276615698,null,null,8.6961583812790089,0.64213836354366127,-0.87316074335734517,-0.87316074335734517]
[8.5,7336,2.7765456079707138,15.913120472779555,7.4450098467727468,8.5212861987749875,8.2870194435506139,47.29654335425468,13.279647924181813,0.99201476031052882,1.9164731535499375,0.19739489832334342,2.799357362218271,2.389920521669386,0.45578606939528615,0.14313889921090869,2.407998368577565,0.22820801682597325,0.19000000000003375,5.6697367976272665E-2,0.93979805867604871,5.2216701634482839E-2,34.15185142219886,0.16373065411075791,0.15913120472779585,2.8023481914232269,27.531138023565791,0.51053310265523677,0.85587801283182863,1.913926466066372,3.1147391514542853,3.5758982006643563,4.3299367784178626,57.962883468947688,3.5786042156871081,0,0,0,0,8.9713720833684285E-2,0.14978483496708578,0.1877717906647775,0.14982302169292916,11.550261071759074,36.339563704047947,3.1355993194835108,3.8110104775893943,3.5758982006643563,3.1147391514542853,1.913926466066372,57.962883468947688,57.962883468947688,4.3299367784178626,0,0,0.2018454905540478,0.1877717906647775,0.14978483496708578,8.9713720833684285E-2,11.550261071759074,11.550261071759074,0.24607254534903178,57.50003595135523,60.496788211896842,13.905392143343514,29.19276839696137,4.13508913366966,2.0723210416109032,0.1780108920089026,0.25574870768312236,null,null,8.353725947541891,0.62403909281813241,-0.85587801283182863,-0.85587801283182863]
[9,7811,4.6981658913645505,12.992645680866216,8.0779247074422305,8.9778785506672332,8.580242496449376,38.743664306428236,12.984636102037753,1.0081271408660961,1.8195317844766028,0.18976355788131116,2.8067875081455855,1.9603347226161669,0.47191333730471369,0.13685550791942569,1.9820156316513238,0.203490205908957,0.190000000000035,5.4505432313957207E-2,0.96669088243971613,4.1436258426381004E-2,28.78725090863065,0.16609825115849114,0.12992645680866238,2.8099868633055038,21.451575683831912,0.46964448992200764,0.82540410799301944,1.8371719644691136,3.1508506166520664,3.7471748568572294,3.7847374544167507,48.747262716421254,3.7240794002776942,0,0,0,0,8.5067327095352682E-2,0.15068200094458914,0.20179519273445912,0.15073357114490146,9.5705287428405086,29.779168741074635,4.0085243568406321,4.0592035678162626,3.7471748568572294,3.1508506166520664,1.8371719644691136,48.747262716421254,48.747262716421254,3.7847374544167507,0,0,0.22184592974809866,0.20179519273445912,0.15068200094458914,8.5067327095352682E-2,9.5705287428405086,9.5705287428405086,0.21540161722654844,49.143438587354218,52.139989653381114,11.001022400545496,25.977281782903969,4.4671701227439913,2.0071380096317548,0.18779443100271459,0.2984486476124823,null,null,8.5110718168721942,0.66079961186612157,-0.82540410799301944,-0.82540410799301944]
[9.5,4714,6.6557330133081303,10.317243084799726,8.8555962676717765,9.4789220240066321,9.1467747332153362,27.428028693531129,12.772372581825392,1.0136964791139509,1.8203317485369239,0.19529293973080417,2.779084737077703,1.396167471403676,0.5030726103268448,0.13914499077775166,1.4303999195286647,0.17408630208878376,0.19000000000002218,5.6093626335508982E-2,0.84955991959931831,0.16413655951463041,20.652804593130213,0.5440457431726019,0.10317243084799695,2.8040672521922496,13.22066337958735,1.4506570427251839,0.76177256073046695,1.6073687471255553,2.9057113116909012,3.6153323209604746,3.0061082958007526,37.876362369181457,3.6510222844929707,0,0,0,0,7.2705198609040761E-2,0.13681552558866916,0.20506543562421634,0.13690900013522078,7.3986086776113495,24.310003469644361,3.3145920980761634,3.9968336293737097,3.6153323209604746,2.9057113116909012,1.6073687471255553,37.876362369181457,37.876362369181457,3.0061082958007526,0,0,0.23292329387839425,0.20506543562421634,0.13681552558866916,7.2705198609040761E-2,7.3986086776113495,7.3986086776113495,0.17127672727530663,38.395135175283386,41.369512852091894,8.3315793719906228,23.089615666625118,4.6083861727779265,1.7916934369717314,0.18568386190149916,0.35348997680720962,null,null,9.0231888160550042,0.71613748147551337,-0.76177256073046695,-0.76177256073046684]
[10,3638,9.1625617492548752,8.0765998557625185,9.5648314919901125,9.979127716600777,10.851208024029328,18.485966237078721,13.245331479227206,1.0163726195054135,2.2306631349635171,0.24497136591280944,2.5682504433712361,0.9601336607465405,0.59681644132161482,0.17283688443336842,1.0265688587458013,0.13920565368358886,0.1900000000000126,7.0362667904706244E-2,0.65232885837101529,0.36404376113439951,14.158626314785847,0.97308792194032623,8.0765998557624882E-2,2.7497057930364854,7.5522801341927579,3.7851541024984701,0.6562574785252886,1.4031799496262425,2.6910935805246448,3.6035658818049741,2.3833180351567447,31.059315048680752,3.7810583171640522,0,0,0,0,6.2316785566059352E-2,0.1249811683562301,0.22860580587628077,0.12523997762572484,6.0522888545181424,21.704737009707852,2.6729971114134181,4.0765337467713234,3.6035658818049741,2.6910935805246448,1.4031799496262425,31.059315048680752,31.059315048680752,2.3833180351567447,0,0,0.27189604256424349,0.22860580587628077,0.1249811683562301,6.2316785566059352E-2,6.0522888545181424,6.0522888545181424,0.13546746490995448,31.567837396071564,34.381059205355612,6.0982953163186373,21.321931334989724,5.1765019171174123,1.6124739670714348,0.20173068159760449,0.42655788150330165,null,null,10.676407270110971,0.81924775088093438,-0.6562574785252886,-0.6562574785252886]
[10.5,4188,11.46452979327818,5.8009465298326166,10.356166442847218,10.525463622254309,10.131846841974497,8.8800565265301312,12.191123723578013,1.013071194183601,1.5336410147023123,0.17561460686804131,1.9265729952259909,0.48553079908116781,0.55725157630860034,0.12181460027308702,0.55309176016473738,9.6848837108265612E-2,0.19000000000001813,5.0441455540031155E-2,0.36713696355918785,0.64593423062441102,7.1309778437328459,1.6284484975290234,5.8009465298326186E-2,2.8026530416747573,3.1821780727926523,6.7360774490081461,0.50685916844063561,1.0447203668994824,1.9821081640939926,3.1214591706797084,1.6852871686857884,20.280454622701889,3.3236972521333978,0,0,0,0,4.69335740919294E-2,9.2717451588731958E-2,0.26058451911648861,9.3060939601317699E-2,3.9637496766944595,19.423208642905355,2.5210747787043837,3.6892958707629977,3.1214591706797084,1.9821081640939926,1.0447203668994824,20.280454622701889,20.280454622701889,1.6852871686857884,0,0,0.34179202144507387,0.26058451911648861,9.2717451588731958E-2,4.69335740919294E-2,3.9637496766944595,3.9637496766944595,9.634030210508604E-2,20.545544383206941,22.647731985300972,3.8357500754734186,17.992070253410631,5.3563303080092242,1.2587618693300622,0.22638852165451392,0.49228044806505084,null,null,10.001120257041165,0.83108391578203655,-0.50685916844063561,-0.50685916844063561]
[11,6498,14.650491357622874,3.8059659695426,10.999816611591694,11.007317086350056,11.448576788616871,2.449657205866306,11.138115691246462,1.0119404014939846,1.0023585116979234,0.11776573728930448,0.76352732988576955,0.13276980923735074,0.62967172337392696,8.0862033623800747E-2,0.19470806512360794,5.1584988321533465E-2,0.19000000000003106,3.3825632773707461E-2,0.14252990110249963,0.86941050039148415,2.4185640062473892,2.0270199514854008,3.8059659695426039E-2,2.7783694877679626,0.73370818401952764,10.652040401051499,0.23166969475423585,0.67852881057190151,1.0724944941112859,3.0167930368575528,1.3378019154435252,14.724772806958311,3.2756729496095756,0,0,0,0,3.0976966848491189E-2,5.0097868442563497E-2,0.57086143613526807,5.0792561175828387E-2,2.8808709042763341,16.968818385049545,2.3314877731205916,3.7941295548513736,3.0167930368575528,1.0724944941112859,0.67852881057190151,14.724772806958311,14.724772806958311,1.3378019154435252,0,0,0.88684342257441062,0.57086143613526807,5.0097868442563497E-2,3.0976966848491189E-2,2.8808709042763341,2.8808709042763341,7.7036877090282646E-2,14.9005925061811,15.781885573356174,1.9217711459793174,14.944081660789061,7.75357281087072,1.0560625892968305,0.46335866132132519,0.49932348722923248,null,null,11.313489185444807,1.0278737540510916,-0.23166969475423585,-0.23166969475423593]
[11.5,4710,16.789973827390209,3.4247706833270057,11.507105297118338,11.464763253953073,18.389427178988349,0.40459067932820886,12.366768447843677,1.0105636945103837,1.2566482805263319,0.15075164039067054,0.19949119787819708,2.1922413488157249E-2,1.0114184948443588,0.10268736058526899,0.11885395503818962,3.8418771889360451E-2,0.19000000000002215,4.3300112114629162E-2,7.9090800316816715E-2,0.93147289419356771,0.93476464514169799,2.1828871683235507,3.4247706833270108E-2,2.7723893459872655,7.4720261072530908E-2,18.315101871665771,8.2852058298269082E-2,0.45208107318379437,0.57331707697326006,2.8379929158158186,1.6213343221720149,19.841071124722525,4.5996326858808274,0,0,0,0,2.6996169125577535E-2,3.4452828707937026E-2,1.0288762191091545,3.6596583433420801E-2,3.8867346019852653,11.818879583937441,2.3434790018376304,3.311683837616187,2.8379929158158186,0.57331707697326006,0.45208107318379437,19.841071124722525,19.841071124722525,1.6213343221720149,0,0,1.3900906677942861,1.0288762191091545,3.4452828707937026E-2,2.6996169125577535E-2,3.8867346019852653,3.8867346019852653,9.2587204178622554E-2,20.050666138842889,20.400908977111758,1.5121933914594536,15.791539131170683,13.259326652321576,1.2918885744862392,0.96632952549801976,0.68905626489461647,null,null,18.197197543196911,1.4870034363904345,-8.285205829826911E-2,-8.2852058298269082E-2]
[12,2039,19.667173013185035,3.5490379677952522,12.023363299533328,11.971292819335444,34.377718265300125,7.3331684657678255E-3,13.905546156655928,1.0033271864254041,1.6902484497315271,0.20236732187046633,1.095989311063391E-2,4.1647859855388329E-4,1.8907745045915054,0.13795163921321105,0.13808876761336722,3.7152961755400352E-2,0.18999999999999798,5.8125587904850909E-2,8.1485067231679642E-2,0.92184211919372394,0.94144546609598634,2.2049000952301649,3.5490379677952592E-2,2.7486048502537863,8.4929201475167479E-4,34.282378921214011,4.7056618342176289E-2,0.45461179574490718,0.53136134053577311,2.6307716048485865,2.5943101750253712,35.955668670779673,7.9713788040122564,0,0,0,0,3.3096624034792993E-2,3.8788391300360194E-2,0.89211225367980451,4.2021141112654342E-2,7.0902874480894846,11.553595009245726,2.3918413460633037,2.8384529436141634,2.6307716048485865,0.53136134053577311,0.45461179574490718,35.955668670779673,35.955668670779673,2.5943101750253712,0,0,1.0289738270214475,0.89211225367980451,3.8788391300360194E-2,3.3096624034792993E-2,7.0902874480894846,7.0902874480894846,0.14702425947960618,36.075299883497422,36.288627098478521,1.6013929820964035,17.454584124451181,22.527449718351331,2.0790313214993046,1.6405719662529934,1.1979960268331957,null,null,34.263716492901054,2.4722307112579776,-4.705661834217615E-2,-4.7056618342176358E-2]
[12.5,930,21.72286450114953,3.6942481285607673,12.495069407453366,12.46241424642869,53.288810555729889,0,15.07802534724037,0.99080944503513357,2.0514916316567904,0.24112044661127788,0,0,2.93088458056515,0.16554052960680662,0.16554052960680662,3.7877278724939664E-2,0.18999999999999825,6.9256575545985799E-2,9.6714983402337307E-2,0.89409446163279682,1.1274914963911948,2.1306008557726175,3.6942481285607578E-2,2.7220333801040875,1.7191938883167157E-3,52.960941864841971,3.7070481196692352E-2,0.53903255735382827,0.61448020671058412,2.6718250604662166,3.6702619151330209,55.853628025744484,11.863551676983512,0,0,0,0,3.9216341585562232E-2,4.4805607585629383E-2,0.78330314535167511,4.8498575682762016E-2,11.142458508216942,11.657878197639713,2.3829706448261749,2.8060561086011591,2.6718250604662166,0.61448020671058412,0.53903255735382827,55.853628025744484,55.853628025744484,3.6702619151330209,0,0,0.85515622868565322,0.78330314535167511,4.4805607585629383E-2,3.9216341585562232E-2,11.142458508216942,11.142458508216942,0.20709477537941434,55.340302187386676,55.581422633997953,1.7219037468805358,18.772273475801136,32.139021874854038,2.9608253206862005,2.2943137331072618,1.7237648042954623,null,null,53.783107158249081,3.5342035398211467,-3.7070481196692241E-2,-3.7070481196692227E-2]
[13,464,23.744602722280749,3.7185122805273356,13.060503000260518,12.955257194443107,70.903764712651551,0,16.876794863046502,1.0080202344555247,2.089879607961783,0.24489830916896657,0,0,3.8997070591958352,0.1683277734783972,0.1683277734783972,3.8514699127517163E-2,0.18999999999999878,7.0341683952618361E-2,0.14327814063080707,0.86474209382471734,1.5027537358645879,2.1944802985938594,3.7185122805273314E-2,2.7219756128781207,0,70.573543697625553,2.8630980510882687E-2,0.55567307188792736,0.62304392617920856,2.6776199566588899,4.3250892668275833,72.412876076877922,15.4951949230477,0,0,0,0,4.0384220522616518E-2,4.5373012723744971E-2,0.77454342009385546,4.9102527376015538E-2,14.218177701019618,10.48836709667261,2.5377280859403601,2.7804323507216284,2.6776199566588899,0.62304392617920856,0.55567307188792736,72.412876076877922,72.412876076877922,4.3250892668275833,0,0,0.82712307352060088,0.77454342009385546,4.5373012723744971E-2,4.0384220522616518E-2,14.218177701019618,14.218177701019618,0.24281222005533146,72.993644320613328,73.238542629782287,1.7596585929357731,20.595307143573837,41.481708220929633,3.5560791649875556,2.9489983459354074,2.2423458878807336,null,null,70.339624433183857,4.201257720321216,-2.8630980510882816E-2,-2.8630980510882427E-2]
[13.5,165,25.364987249751529,3.5014753297817323,13.493269665065702,13.469883733833289,84.404571639961588,0,17.614344383816416,1.0113805883612634,1.6321361573481468,0.1976363731554924,0,0,4.6422514401978869,0.13414675656959041,0.13414675656959041,3.5277416506289946E-2,0.19000000000000056,5.676672634131464E-2,0.1118241766558517,0.89955641170541123,1.0697327378128851,1.8146634183367534,3.5014753297817301E-2,2.7828651092756385,0,84.304789918325241,1.8970230255593086E-2,0.47704696021343057,0.51972407890751204,3.0215792506520867,4.8844683584339332,85.068577336168502,19.108596803141452,0,0,0,0,3.524805049826138E-2,3.8456948402053111E-2,1.2097810333401871,4.1700316776709608E-2,16.651973224475118,9.5662026746244457,2.0172869591318343,3.1328562184998954,3.0215792506520867,0.51972407890751204,0.47704696021343057,85.068577336168502,85.068577336168502,4.8844683584339332,0,0,1.2936909594376391,1.2097810333401871,3.8456948402053111E-2,3.524805049826138E-2,16.651973224475118,16.651973224475118,0.27376354084991233,86.036707797309731,86.234344170465221,1.5323544357118648,21.11581971359815,56.146741114330275,4.083873860456011,4.2303685298910727,3.063985237601734,null,null,83.454806836585661,4.7918088689982827,-1.8970230255593055E-2,-1.8970230255593086E-2]
[14,110,27.714326281770138,3.4389979740406766,14.382108836762287,13.969588230639243,92.517715600098882,0,16.713244720239928,0.99439833890105167,1.0495200949013768,0.1288120662381918,0,0,5.0884743580054357,8.6981118813190234E-2,8.6981118813190234E-2,3.7471012642383311E-2,0.19000000000000017,3.6998449206764948E-2,6.3912679109792384E-2,0.9304856597912593,0.58792086109803832,2.1968721303452177,3.4389979740406751E-2,2.8626374647720207,0,92.910142287128934,1.1216747904389117E-2,0.32492572313335327,0.34153051774828014,2.2880198355646577,5.5983884195562146,94.094320188029528,21.134146633299185,0,0,0,0,2.4218924483475558E-2,2.5482218188963804E-2,1.0493634384179718,2.7646727289840859E-2,18.708654164630609,9.1988142147519518,2.3609951504658904,2.3450424445559674,2.2880198355646577,0.34153051774828014,0.32492572313335327,94.094320188029528,94.094320188029528,5.5983884195562146,0,0,1.0981915132067297,1.0493634384179718,2.5482218188963804E-2,2.4218924483475558E-2,18.708654164630609,18.708654164630609,0.31441999965780637,93.567235695000264,93.696047761238461,1.4419467819315157,20.152242694280606,64.889520797477104,4.6494104493804196,4.998424032338348,3.5682386690089207,null,null,93.038887919245539,5.5355927079832012,-1.1216747904389009E-2,-1.1216747904389092E-2]
[14.5,31,27.692086214058929,3.2977589452157168,15.075274781553611,14.374901458249369,99.24062881490353,0,16.454678402065174,0.97574805140482024,0.95903542580153289,0.11806590681451226,0,0,5.4582345848196949,7.963571286584667E-2,7.963571286584667E-2,3.8322779142794618E-2,0.19000000000000011,3.3911849905814348E-2,3.309574158123664E-2,0.9426523098235835,0.48795692818064101,2.1538256201589072,3.2977589452157174E-2,2.868390001811711,0,99.568644477096328,9.5712439065433006E-3,0.31172885287403057,0.32569379877212912,2.9909835570334145,6.0894331564772077,102.69009924892387,23.474333896457924,0,0,0,0,2.33056240185875E-2,2.4374210752346172E-2,1.9360028620449998,2.6443374181238054E-2,20.778400075384432,14.743797989324531,2.2848568848910937,3.0807133663337383,2.9909835570334145,0.32569379877212912,0.31172885287403057,102.69009924892387,102.69009924892387,6.0894331564772077,0,0,2.0498668907539566,1.9360028620449998,2.4374210752346172E-2,2.33056240185875E-2,20.778400075384432,20.778400075384432,0.34222019267255327,100.19966424070506,100.31773014751957,1.2870510879943136,19.752437347280889,77.852126598060707,5.0787519729219266,6.3594569700153825,4.2886486393638048,null,null,101.70722726222529,6.0311497064839727,-9.5712439065432434E-3,-9.5712439065432624E-3]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,{"$f":"CELL(\"filename\")","v":"/Users/signhildgehlin/Dropbox/Gehlin-Spitler_collaboration/Studenthuset/studenthuset data detailed excel files/2021_update/20211208_Results/[BinResultsHPEFT_V2.xlsm]Plot (2)"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[]
[null,null,null,null,null,null,null,null,{"$f":"CELL(\"filename\")","v":"/Users/signhildgehlin/Dropbox/Gehlin-Spitler_collaboration/Studenthuset/studenthuset data detailed excel files/2021_update/20211208_Results/[BinResultsHPEFT_V2.xlsm]Plot (2)"}]
[]
[]
[]
[]
[]
[]
[]
[]
[]
["HP EFT / BH ExFT (°C)","Hours"]
[6.5,36,null,6.45,0]
[7,271,null,6.45,36]
[7.5,1041,null,6.55,36]
[8,2951,null,6.55,0]
[8.5,7336]
[9,7811,null,6.95,0]
[9.5,4714,null,6.95,271]
[10,3638,null,7.05,271]
[10.5,4188,null,7.05,0]
[11,6498]
[11.5,4710,null,7.45,0]
[12,2039,null,7.45,1041]
[12.5,930,null,7.55,1041]
[13,464,null,7.55,0]
[13.5,165]
[14,110,null,7.95,0]
[14.5,31,null,7.95,2951]
[null,null,null,8.0500000000000007,2951]
[null,null,null,8.0500000000000007,0]
[]
[null,null,null,8.4499999999999993,0]
[null,null,null,8.4499999999999993,7336]
[null,null,null,8.5500000000000007,7336]
[null,null,null,8.5500000000000007,0]
[]
[null,null,null,8.9499999999999993,0]
[null,null,null,8.9499999999999993,7811]
[null,null,null,9.0500000000000007,7811]
[null,null,null,9.0500000000000007,0]
[]
[null,null,null,9.4499999999999993,0]
[null,null,null,9.4499999999999993,4714]
[null,null,null,9.5500000000000007,4714]
[null,null,null,9.5500000000000007,0]
[]
[null,null,null,9.9499999999999993,0]
[null,null,null,9.9499999999999993,3638]
[null,null,null,10.050000000000001,3638]
[null,null,null,10.050000000000001,0]
[]
[null,null,null,10.45,0]
[null,null,null,10.45,4188]
[null,null,null,10.55,4188]
[null,null,null,10.55,0]
[]
[null,null,null,10.95,0]
[null,null,null,10.95,6498]
[null,null,null,11.05,6498]
[null,null,null,11.05,0]
[]
[null,null,null,11.45,0]
[null,null,null,11.45,4710]
[null,null,null,11.55,4710]
[null,null,null,11.55,0]
[]
[null,null,null,11.95,0]
[null,null,null,11.95,2039]
[null,null,null,12.05,2039]
[null,null,null,12.05,0]
[]
[null,null,null,12.45,0]
[null,null,null,12.45,930]
[null,null,null,12.55,930]
[null,null,null,12.55,0]
[]
[null,null,null,12.95,0]
[null,null,null,12.95,464]
[null,null,null,13.05,464]
[null,null,null,13.05,0]
[]
[null,null,null,13.45,0]
[null,null,null,13.45,165]
[null,null,null,13.55,165]
[null,null,null,13.55,0]
[]
[null,null,null,13.95,0]
[null,null,null,13.95,110]
[null,null,null,14.05,110]
[null,null,null,14.05,0]
[]
[null,null,null,14.45,0]
[null,null,null,14.45,31]
[null,null,null,14.55,31]
[null,null,null,14.55,0]

{"sheet":"Plot5","index":5,"n_rows":42,"n_cols":70,"rows_kept":42,"cut":false,"hidden":false,"merged":[]}
[]
["HP EFT / BH ExFT (°C)","Count","ODA Temperature (°C)","EL 007 (kW)","GHE EFT (°C)","GHE ExFT (°C)","Clg Provided (kW)","Bldg Htg Provided (kW)","EL 003 (kW)","CP Energy (kW)","DHW Provided by HP (kW)","DHW by LPS (kW)","Useful Bldg Htg by LPS (kW)","Bldg Htg Uncertainty (kW)","Bldg Clg Uncertainty (kW)","DHW Htg by HP Uncertainty (kW)","Bldg + DHW Htg by HP Uncertainty (kW)","EL007+EL011 Uncertainty (kW)","EL011 Uncertainty (kW)","LPS DHW Uncertainty (kW)","CP Power for Heat Extraction from GHE (kW)","CP Power for Heat Rejection to GHE (kW)","Heat Extraction by GHE (kW)","Heat Rejection to GHE (kW)","EL007 Uncertainty (kW)","LPS Electricity going to bldg heat (kW)","Alt Calc GHE Heat Extraction (kW)","Alt Calc GHE Heat Extraction (kW)","HtgFrac","COP H4","COP H3","COP H2","COP C3","COP C2","Overall (H+C) COP","Not used","Not used","Not used","Not used","Error COP H4","Error COP H3","Error COP H2","Error COP H3b","Error COP C2","BPF0, heating","BPF0, cooling","BPF1*, heating","BPF2, heating","BPF3+, heating","BPF4+, heating","BPF2, cooling","BPF3, cooling","BPF4, cooling","Error BPF0, heating","Error BPF0, cooling","Error BPF1*, heating","Error BPF2, heating","Error BPF3+, heating","Error BPF4+, heating","Error BPF2, cooling","Error BPF3, cooling","Error BPF4, cooling","Htg & Clg Provided Boundary 2","Htg & Clg Provided Boundary 4+","Electricity Used Boundary 2","Electricity Used Boundary 4+","BPFHC2","BPFHC4+","Error BPFHC2","Error BPFHC4+"]
[6.5,36,-7.0411861459593581,30.484337959459669,5.2780850062215929,6.6402453190685424,8.0436702536399949,104.75341582045593,14.993770169517253,1.0589186309565459,4.2940337543861498,0.43627920977577606,2.4035603732898521,5.2631852146390337,0.44240186395019976,0.31829755733395204,5.2931230985630497,0.35627645845993844,0.19000000000000014,0.12531166259695264,0.99518451049720036,6.3734120459345595E-2,52.574276917265792,0.43414671121875065,0.30484337959459668,2.5608379621679296,73.388006323535535,0.93036642080595888,0.93130418203000731,2.5172570283410152,3.5553055032715042,3.8298013011981622,7.8093180370692474,110.57612587542329,3.8021108907311207,0,0,0,0,0.12078274552885053,0.17294200809607552,0.19304429275198728,0.17298784204666051,20.751673115392062,52.828672836758038,6.8118412569242563,3.9672053576390969,3.8298013011981622,3.5553055032715042,2.5172570283410152,110.57612587542329,110.57612587542329,7.8093180370692474,0,0,0.20044469583491742,0.19304429275198728,0.17294200809607552,0.12078274552885053,20.751673115392062,20.751673115392062,0.44076511874953817,117.09111982848208,119.9309594115477,28.546139418472507,45.47810812897692,4.1018197981864821,2.6371140829214101,0.18725152918687613,0.20166772099798613]
[7,271,-6.5215819137791078,27.573372148678338,5.3323478659701884,7.0662003087664926,7.5550134740443395,89.50567159290307,14.02168824167614,1.0647245464717638,3.121082755977334,0.31744130618210653,2.6063791678716934,4.4959644291915088,0.41552574107243867,0.23146982925756227,4.5108365176366902,0.32786125813451489,0.18999999999999947,9.1178073498098491E-2,1.0155488452051573,4.9175701266606975E-2,60.31582591058239,9.2337358929828514E-2,0.2757337214867831,2.6698502606884253,59.97888031224506,0.5579445656885017,0.92458694193340529,2.3570827040473743,3.345865796869167,3.6224052921654954,7.1447721626814022,94.091723680930116,3.6002947191123775,0,0,0,0,0.11289643986997469,0.16255825722836023,0.18337879295982334,0.16258960815219256,17.57006945846172,59.392343554285283,1.8777029417276596,3.7674469519724316,3.6224052921654954,3.345865796869167,2.3570827040473743,94.091723680930116,94.091723680930116,7.1447721626814022,0,0,0.19126250100203224,0.18337879295982334,0.16255825722836023,0.11289643986997469,17.57006945846172,17.57006945846172,0.40471299002918831,100.18176782292474,103.10558829697854,25.650805128279572,41.595060390354476,3.9055993494908301,2.4787940522112528,0.17793880666221265,0.20016022613252341]
[7.5,1041,-3.6273399084647271,22.303652351738521,6.1154874257299721,7.5505014614738633,7.0268158392849003,69.555186852758169,12.987059083453744,1.0173398289775222,2.1037282465901885,0.21395119728546155,2.7780209203683399,3.505530250084929,0.38647487116067042,0.15601290764450551,3.5211063789260169,0.28234549224996397,0.1899999999999982,6.1452802805407512E-2,0.94284627267708898,7.4493556300432404E-2,46.534465672831175,0.150903995833473,0.22303652351738509,2.7843204485575166,44.931870863455089,0.62249213826467975,0.91069771157409618,2.1871912416376822,3.2135356351340008,3.5418829771673956,6.0587797770846734,77.344588993155313,3.5023253909336569,0,0,0,0,0.10473927632490038,0.15652633272455019,0.18211132280670111,0.15654868549043538,15.058355867336132,49.355305335940535,2.0257322019219677,3.7118623139850806,3.5418829771673956,3.2135356351340008,2.1871912416376822,77.344588993155313,77.344588993155313,6.0587797770846734,0,0,0.19163348841826727,0.18211132280670111,0.15652633272455019,0.10473927632490038,15.058355867336132,15.058355867336132,0.34482044907702647,78.685730938633256,81.677703056287058,20.322720534873067,35.290711435192264,3.871810902659973,2.3144249502104737,0.17545458270629355,0.21505965603755475]
[8,2951,0.71646430629359581,18.838658405575497,6.7897360586838165,8.0389630307381736,8.5594676452811207,56.899907175400621,13.329631324385328,0.98428148039573959,2.0234208992252007,0.20593269951882195,2.7894102974310733,2.872027469464502,0.4707707204904637,0.15012025069236817,2.8892086945585618,0.25107135743355719,0.19000000000000283,5.9149664667827923E-2,0.9292558670506269,5.502561334511219E-2,39.759367537750109,0.15821245017054544,0.18838658405575526,2.7940130217421184,34.25461462466771,0.71374836003336084,0.87316074335734517,2.0316144854695111,3.1433838196076,3.5287341949233597,5.0626153175334538,68.56046472882413,3.5553827596851288,0,0,0,0,9.6263900445057934E-2,0.15204821617232761,0.18296969115640341,0.15207786465563247,13.761232512828682,42.786243216244308,2.8752510068040729,3.7202094165758148,3.5287341949233597,3.1433838196076,2.0316144854695111,68.56046472882413,68.56046472882413,5.0626153175334538,0,0,0.19399149053892095,0.18296969115640341,0.15204821617232761,9.6263900445057934E-2,13.761232512828682,13.761232512828682,0.28764278463380499,67.482795719906946,70.478138716856847,16.822994164710298,32.168289729960826,4.0113427526157048,2.1909196699137872,0.17538878805268146,0.2316952276615698]
[8.5,7336,2.7765456079707138,15.913120472779555,7.4450098467727468,8.5212861987749875,8.2870194435506139,47.29654335425468,13.279647924181813,0.99201476031052882,1.9164731535499375,0.19739489832334342,2.799357362218271,2.389920521669386,0.45578606939528615,0.14313889921090869,2.407998368577565,0.22820801682597325,0.19000000000003375,5.6697367976272665E-2,0.93979805867604871,5.2216701634482839E-2,34.15185142219886,0.16373065411075791,0.15913120472779585,2.8023481914232269,27.531138023565791,0.51053310265523677,0.85587801283182863,1.913926466066372,3.1147391514542853,3.5758982006643563,4.3299367784178626,57.962883468947688,3.5786042156871081,0,0,0,0,8.9713720833684285E-2,0.14978483496708578,0.1877717906647775,0.14982302169292916,11.550261071759074,36.339563704047947,3.1355993194835108,3.8110104775893943,3.5758982006643563,3.1147391514542853,1.913926466066372,57.962883468947688,57.962883468947688,4.3299367784178626,0,0,0.2018454905540478,0.1877717906647775,0.14978483496708578,8.9713720833684285E-2,11.550261071759074,11.550261071759074,0.24607254534903178,57.50003595135523,60.496788211896842,13.905392143343514,29.19276839696137,4.13508913366966,2.0723210416109032,0.1780108920089026,0.25574870768312236]
[9,7811,4.6981658913645505,12.992645680866216,8.0779247074422305,8.9778785506672332,8.580242496449376,38.743664306428236,12.984636102037753,1.0081271408660961,1.8195317844766028,0.18976355788131116,2.8067875081455855,1.9603347226161669,0.47191333730471369,0.13685550791942569,1.9820156316513238,0.203490205908957,0.190000000000035,5.4505432313957207E-2,0.96669088243971613,4.1436258426381004E-2,28.78725090863065,0.16609825115849114,0.12992645680866238,2.8099868633055038,21.451575683831912,0.46964448992200764,0.82540410799301944,1.8371719644691136,3.1508506166520664,3.7471748568572294,3.7847374544167507,48.747262716421254,3.7240794002776942,0,0,0,0,8.5067327095352682E-2,0.15068200094458914,0.20179519273445912,0.15073357114490146,9.5705287428405086,29.779168741074635,4.0085243568406321,4.0592035678162626,3.7471748568572294,3.1508506166520664,1.8371719644691136,48.747262716421254,48.747262716421254,3.7847374544167507,0,0,0.22184592974809866,0.20179519273445912,0.15068200094458914,8.5067327095352682E-2,9.5705287428405086,9.5705287428405086,0.21540161722654844,49.143438587354218,52.139989653381114,11.001022400545496,25.977281782903969,4.4671701227439913,2.0071380096317548,0.18779443100271459,0.2984486476124823]
[9.5,4714,6.6557330133081303,10.317243084799726,8.8555962676717765,9.4789220240066321,9.1467747332153362,27.428028693531129,12.772372581825392,1.0136964791139509,1.8203317485369239,0.19529293973080417,2.779084737077703,1.396167471403676,0.5030726103268448,0.13914499077775166,1.4303999195286647,0.17408630208878376,0.19000000000002218,5.6093626335508982E-2,0.84955991959931831,0.16413655951463041,20.652804593130213,0.5440457431726019,0.10317243084799695,2.8040672521922496,13.22066337958735,1.4506570427251839,0.76177256073046695,1.6073687471255553,2.9057113116909012,3.6153323209604746,3.0061082958007526,37.876362369181457,3.6510222844929707,0,0,0,0,7.2705198609040761E-2,0.13681552558866916,0.20506543562421634,0.13690900013522078,7.3986086776113495,24.310003469644361,3.3145920980761634,3.9968336293737097,3.6153323209604746,2.9057113116909012,1.6073687471255553,37.876362369181457,37.876362369181457,3.0061082958007526,0,0,0.23292329387839425,0.20506543562421634,0.13681552558866916,7.2705198609040761E-2,7.3986086776113495,7.3986086776113495,0.17127672727530663,38.395135175283386,41.369512852091894,8.3315793719906228,23.089615666625118,4.6083861727779265,1.7916934369717314,0.18568386190149916,0.35348997680720962]
[10,3638,9.1625617492548752,8.0765998557625185,9.5648314919901125,9.979127716600777,10.851208024029328,18.485966237078721,13.245331479227206,1.0163726195054135,2.2306631349635171,0.24497136591280944,2.5682504433712361,0.9601336607465405,0.59681644132161482,0.17283688443336842,1.0265688587458013,0.13920565368358886,0.1900000000000126,7.0362667904706244E-2,0.65232885837101529,0.36404376113439951,14.158626314785847,0.97308792194032623,8.0765998557624882E-2,2.7497057930364854,7.5522801341927579,3.7851541024984701,0.6562574785252886,1.4031799496262425,2.6910935805246448,3.6035658818049741,2.3833180351567447,31.059315048680752,3.7810583171640522,0,0,0,0,6.2316785566059352E-2,0.1249811683562301,0.22860580587628077,0.12523997762572484,6.0522888545181424,21.704737009707852,2.6729971114134181,4.0765337467713234,3.6035658818049741,2.6910935805246448,1.4031799496262425,31.059315048680752,31.059315048680752,2.3833180351567447,0,0,0.27189604256424349,0.22860580587628077,0.1249811683562301,6.2316785566059352E-2,6.0522888545181424,6.0522888545181424,0.13546746490995448,31.567837396071564,34.381059205355612,6.0982953163186373,21.321931334989724,5.1765019171174123,1.6124739670714348,0.20173068159760449,0.42655788150330165]
[10.5,4188,11.46452979327818,5.8009465298326166,10.356166442847218,10.525463622254309,10.131846841974497,8.8800565265301312,12.191123723578013,1.013071194183601,1.5336410147023123,0.17561460686804131,1.9265729952259909,0.48553079908116781,0.55725157630860034,0.12181460027308702,0.55309176016473738,9.6848837108265612E-2,0.19000000000001813,5.0441455540031155E-2,0.36713696355918785,0.64593423062441102,7.1309778437328459,1.6284484975290234,5.8009465298326186E-2,2.8026530416747573,3.1821780727926523,6.7360774490081461,0.50685916844063561,1.0447203668994824,1.9821081640939926,3.1214591706797084,1.6852871686857884,20.280454622701889,3.3236972521333978,0,0,0,0,4.69335740919294E-2,9.2717451588731958E-2,0.26058451911648861,9.3060939601317699E-2,3.9637496766944595,19.423208642905355,2.5210747787043837,3.6892958707629977,3.1214591706797084,1.9821081640939926,1.0447203668994824,20.280454622701889,20.280454622701889,1.6852871686857884,0,0,0.34179202144507387,0.26058451911648861,9.2717451588731958E-2,4.69335740919294E-2,3.9637496766944595,3.9637496766944595,9.634030210508604E-2,20.545544383206941,22.647731985300972,3.8357500754734186,17.992070253410631,5.3563303080092242,1.2587618693300622,0.22638852165451392,0.49228044806505084]
[11,6498,14.650491357622874,3.8059659695426,10.999816611591694,11.007317086350056,11.448576788616871,2.449657205866306,11.138115691246462,1.0119404014939846,1.0023585116979234,0.11776573728930448,0.76352732988576955,0.13276980923735074,0.62967172337392696,8.0862033623800747E-2,0.19470806512360794,5.1584988321533465E-2,0.19000000000003106,3.3825632773707461E-2,0.14252990110249963,0.86941050039148415,2.4185640062473892,2.0270199514854008,3.8059659695426039E-2,2.7783694877679626,0.73370818401952764,10.652040401051499,0.23166969475423585,0.67852881057190151,1.0724944941112859,3.0167930368575528,1.3378019154435252,14.724772806958311,3.2756729496095756,0,0,0,0,3.0976966848491189E-2,5.0097868442563497E-2,0.57086143613526807,5.0792561175828387E-2,2.8808709042763341,16.968818385049545,2.3314877731205916,3.7941295548513736,3.0167930368575528,1.0724944941112859,0.67852881057190151,14.724772806958311,14.724772806958311,1.3378019154435252,0,0,0.88684342257441062,0.57086143613526807,5.0097868442563497E-2,3.0976966848491189E-2,2.8808709042763341,2.8808709042763341,7.7036877090282646E-2,14.9005925061811,15.781885573356174,1.9217711459793174,14.944081660789061,7.75357281087072,1.0560625892968305,0.46335866132132519,0.49932348722923248]
[11.5,4710,16.789973827390209,3.4247706833270057,11.507105297118338,11.464763253953073,18.389427178988349,0.40459067932820886,12.366768447843677,1.0105636945103837,1.2566482805263319,0.15075164039067054,0.19949119787819708,2.1922413488157249E-2,1.0114184948443588,0.10268736058526899,0.11885395503818962,3.8418771889360451E-2,0.19000000000002215,4.3300112114629162E-2,7.9090800316816715E-2,0.93147289419356771,0.93476464514169799,2.1828871683235507,3.4247706833270108E-2,2.7723893459872655,7.4720261072530908E-2,18.315101871665771,8.2852058298269082E-2,0.45208107318379437,0.57331707697326006,2.8379929158158186,1.6213343221720149,19.841071124722525,4.5996326858808274,0,0,0,0,2.6996169125577535E-2,3.4452828707937026E-2,1.0288762191091545,3.6596583433420801E-2,3.8867346019852653,11.818879583937441,2.3434790018376304,3.311683837616187,2.8379929158158186,0.57331707697326006,0.45208107318379437,19.841071124722525,19.841071124722525,1.6213343221720149,0,0,1.3900906677942861,1.0288762191091545,3.4452828707937026E-2,2.6996169125577535E-2,3.8867346019852653,3.8867346019852653,9.2587204178622554E-2,20.050666138842889,20.400908977111758,1.5121933914594536,15.791539131170683,13.259326652321576,1.2918885744862392,0.96632952549801976,0.68905626489461647]
[12,2039,19.667173013185035,3.5490379677952522,12.023363299533328,11.971292819335444,34.377718265300125,7.3331684657678255E-3,13.905546156655928,1.0033271864254041,1.6902484497315271,0.20236732187046633,1.095989311063391E-2,4.1647859855388329E-4,1.8907745045915054,0.13795163921321105,0.13808876761336722,3.7152961755400352E-2,0.18999999999999798,5.8125587904850909E-2,8.1485067231679642E-2,0.92184211919372394,0.94144546609598634,2.2049000952301649,3.5490379677952592E-2,2.7486048502537863,8.4929201475167479E-4,34.282378921214011,4.7056618342176289E-2,0.45461179574490718,0.53136134053577311,2.6307716048485865,2.5943101750253712,35.955668670779673,7.9713788040122564,0,0,0,0,3.3096624034792993E-2,3.8788391300360194E-2,0.89211225367980451,4.2021141112654342E-2,7.0902874480894846,11.553595009245726,2.3918413460633037,2.8384529436141634,2.6307716048485865,0.53136134053577311,0.45461179574490718,35.955668670779673,35.955668670779673,2.5943101750253712,0,0,1.0289738270214475,0.89211225367980451,3.8788391300360194E-2,3.3096624034792993E-2,7.0902874480894846,7.0902874480894846,0.14702425947960618,36.075299883497422,36.288627098478521,1.6013929820964035,17.454584124451181,22.527449718351331,2.0790313214993046,1.6405719662529934,1.1979960268331957]
[12.5,930,21.72286450114953,3.6942481285607673,12.495069407453366,12.46241424642869,53.288810555729889,0,15.07802534724037,0.99080944503513357,2.0514916316567904,0.24112044661127788,0,0,2.93088458056515,0.16554052960680662,0.16554052960680662,3.7877278724939664E-2,0.18999999999999825,6.9256575545985799E-2,9.6714983402337307E-2,0.89409446163279682,1.1274914963911948,2.1306008557726175,3.6942481285607578E-2,2.7220333801040875,1.7191938883167157E-3,52.960941864841971,3.7070481196692352E-2,0.53903255735382827,0.61448020671058412,2.6718250604662166,3.6702619151330209,55.853628025744484,11.863551676983512,0,0,0,0,3.9216341585562232E-2,4.4805607585629383E-2,0.78330314535167511,4.8498575682762016E-2,11.142458508216942,11.657878197639713,2.3829706448261749,2.8060561086011591,2.6718250604662166,0.61448020671058412,0.53903255735382827,55.853628025744484,55.853628025744484,3.6702619151330209,0,0,0.85515622868565322,0.78330314535167511,4.4805607585629383E-2,3.9216341585562232E-2,11.142458508216942,11.142458508216942,0.20709477537941434,55.340302187386676,55.581422633997953,1.7219037468805358,18.772273475801136,32.139021874854038,2.9608253206862005,2.2943137331072618,1.7237648042954623]
[13,464,23.744602722280749,3.7185122805273356,13.060503000260518,12.955257194443107,70.903764712651551,0,16.876794863046502,1.0080202344555247,2.089879607961783,0.24489830916896657,0,0,3.8997070591958352,0.1683277734783972,0.1683277734783972,3.8514699127517163E-2,0.18999999999999878,7.0341683952618361E-2,0.14327814063080707,0.86474209382471734,1.5027537358645879,2.1944802985938594,3.7185122805273314E-2,2.7219756128781207,0,70.573543697625553,2.8630980510882687E-2,0.55567307188792736,0.62304392617920856,2.6776199566588899,4.3250892668275833,72.412876076877922,15.4951949230477,0,0,0,0,4.0384220522616518E-2,4.5373012723744971E-2,0.77454342009385546,4.9102527376015538E-2,14.218177701019618,10.48836709667261,2.5377280859403601,2.7804323507216284,2.6776199566588899,0.62304392617920856,0.55567307188792736,72.412876076877922,72.412876076877922,4.3250892668275833,0,0,0.82712307352060088,0.77454342009385546,4.5373012723744971E-2,4.0384220522616518E-2,14.218177701019618,14.218177701019618,0.24281222005533146,72.993644320613328,73.238542629782287,1.7596585929357731,20.595307143573837,41.481708220929633,3.5560791649875556,2.9489983459354074,2.2423458878807336]
[13.5,165,25.364987249751529,3.5014753297817323,13.493269665065702,13.469883733833289,84.404571639961588,0,17.614344383816416,1.0113805883612634,1.6321361573481468,0.1976363731554924,0,0,4.6422514401978869,0.13414675656959041,0.13414675656959041,3.5277416506289946E-2,0.19000000000000056,5.676672634131464E-2,0.1118241766558517,0.89955641170541123,1.0697327378128851,1.8146634183367534,3.5014753297817301E-2,2.7828651092756385,0,84.304789918325241,1.8970230255593086E-2,0.47704696021343057,0.51972407890751204,3.0215792506520867,4.8844683584339332,85.068577336168502,19.108596803141452,0,0,0,0,3.524805049826138E-2,3.8456948402053111E-2,1.2097810333401871,4.1700316776709608E-2,16.651973224475118,9.5662026746244457,2.0172869591318343,3.1328562184998954,3.0215792506520867,0.51972407890751204,0.47704696021343057,85.068577336168502,85.068577336168502,4.8844683584339332,0,0,1.2936909594376391,1.2097810333401871,3.8456948402053111E-2,3.524805049826138E-2,16.651973224475118,16.651973224475118,0.27376354084991233,86.036707797309731,86.234344170465221,1.5323544357118648,21.11581971359815,56.146741114330275,4.083873860456011,4.2303685298910727,3.063985237601734]
[14,110,27.714326281770138,3.4389979740406766,14.382108836762287,13.969588230639243,92.517715600098882,0,16.713244720239928,0.99439833890105167,1.0495200949013768,0.1288120662381918,0,0,5.0884743580054357,8.6981118813190234E-2,8.6981118813190234E-2,3.7471012642383311E-2,0.19000000000000017,3.6998449206764948E-2,6.3912679109792384E-2,0.9304856597912593,0.58792086109803832,2.1968721303452177,3.4389979740406751E-2,2.8626374647720207,0,92.910142287128934,1.1216747904389117E-2,0.32492572313335327,0.34153051774828014,2.2880198355646577,5.5983884195562146,94.094320188029528,21.134146633299185,0,0,0,0,2.4218924483475558E-2,2.5482218188963804E-2,1.0493634384179718,2.7646727289840859E-2,18.708654164630609,9.1988142147519518,2.3609951504658904,2.3450424445559674,2.2880198355646577,0.34153051774828014,0.32492572313335327,94.094320188029528,94.094320188029528,5.5983884195562146,0,0,1.0981915132067297,1.0493634384179718,2.5482218188963804E-2,2.4218924483475558E-2,18.708654164630609,18.708654164630609,0.31441999965780637,93.567235695000264,93.696047761238461,1.4419467819315157,20.152242694280606,64.889520797477104,4.6494104493804196,4.998424032338348,3.5682386690089207]
[14.5,31,27.692086214058929,3.2977589452157168,15.075274781553611,14.374901458249369,99.24062881490353,0,16.454678402065174,0.97574805140482024,0.95903542580153289,0.11806590681451226,0,0,5.4582345848196949,7.963571286584667E-2,7.963571286584667E-2,3.8322779142794618E-2,0.19000000000000011,3.3911849905814348E-2,3.309574158123664E-2,0.9426523098235835,0.48795692818064101,2.1538256201589072,3.2977589452157174E-2,2.868390001811711,0,99.568644477096328,9.5712439065433006E-3,0.31172885287403057,0.32569379877212912,2.9909835570334145,6.0894331564772077,102.69009924892387,23.474333896457924,0,0,0,0,2.33056240185875E-2,2.4374210752346172E-2,1.9360028620449998,2.6443374181238054E-2,20.778400075384432,14.743797989324531,2.2848568848910937,3.0807133663337383,2.9909835570334145,0.32569379877212912,0.31172885287403057,102.69009924892387,102.69009924892387,6.0894331564772077,0,0,2.0498668907539566,1.9360028620449998,2.4374210752346172E-2,2.33056240185875E-2,20.778400075384432,20.778400075384432,0.34222019267255327,100.19966424070506,100.31773014751957,1.2870510879943136,19.752437347280889,77.852126598060707,5.0787519729219266,6.3594569700153825,4.2886486393638048]
[]
[]
[null,null,null,null,null,null,null,null,null,null,{"$f":"CELL(\"filename\")","v":"/Users/signhildgehlin/Dropbox/Gehlin-Spitler_collaboration/Studenthuset/studenthuset data detailed excel files/2021_update/20211208_Results/[BinResultsHPEFT_V2.xlsm]Plot (2)"}]
[]
[]
["HP EFT / BH ExFT (°C)","Bldg+DHW HP Heating Provided (kWj)","HP Htg. Elec. (kWh)","BPFH1*","Boundary 2 Elec.",null,null,null,null,null,null,null,null,null,null,"HP EFT / BH ExFT (°C)","Clg. Provided","Clg LSCP"]
[6.5,{"$f":"B3*(H3+K3)","v":3925.7081846943147},{"$f":"B3*(D3-L3-M3)","v":995.20194155018544},{"$f":"B26/C26","v":3.9446347728978495},null,null,null,null,null,null,null,null,null,null,null,6.5,{"$f":"B3*G3","v":289.57212913103979},{"$f":"B3*V3","v":2.2944283365364413}]
[7,{"$f":"B4*(H4+K4)","v":25101.85042854659},{"$f":"B4*(D4-L4-M4)","v":6680.0285038232496},{"$f":"B27/C27","v":3.757746005751291},null,null,null,null,null,null,null,null,null,null,null,7,{"$f":"B4*G4","v":2047.408651466016},{"$f":"B4*V4","v":13.32661504325049}]
[7.5,74596.93061842164,20103.459123682191,3.7106514933315773,null,null,null,null,null,null,null,null,null,null,null,7.5,7314.9152886955808,77.54779210875013,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"Figure 9 for B&W"]
[8,173882.74114822081,46753.623770854152,3.7191286391070713,null,null,null,null,null,null,null,null,null,null,null,8,25258.989021224588,162.38058498142607]
[8.5,361026.68910125468,94754.477204977535,3.8101280250880816,null,null,null,null,null,null,null,null,null,null,null,8.5,60793.574637887301,383.06172319056611]
[9,316839.1246660577,78079.495036509921,4.0579043770442409,null,null,null,null,null,null,null,null,null,null,null,9,67020.274139766072,323.65861456846204]
[9.5,137876.77112390878,34614.267533270606,3.9832352653825227,null,null,null,null,null,null,null,null,null,null,null,9.5,43117.896092377094,773.73974155196777]
[10,75367.097655489662,19148.169333088688,3.9359949426211074,null,null,null,null,null,null,null,null,null,null,null,10,39476.694791418697,1324.3912030069455]
[10.5,43612.565302681469,15490.402389369192,2.8154572235393998,null,null,null,null,null,null,null,null,null,null,null,10.5,42432.174574189194,2705.1725578550336]
[11,22431.198132732363,19004.524519584182,1.1803083055099322,null,null,null,null,null,null,null,null,null,null,null,11,74392.851972432429,5649.4294315438638]
[11.5,7824.4355009148867,14481.026150223832,0.5403232767999625,null,null,null,null,null,null,null,null,null,null,null,11.5,86614.20201303513,4387.2373316517042]
[12,3461.3689195042843,6801.5142249880555,0.50891151661310585,null,null,null,null,null,null,null,null,null,null,null,12,70096.167542946961,1879.6360810360031]
[12.5,1907.887217440815,3211.4087442130253,0.59409666268077443,null,null,null,null,null,null,null,null,null,null,null,12.5,49558.593816828798,831.50784931850103]
[13,969.70413809426725,1611.7568827102832,0.60164417381834978,null,null,null,null,null,null,null,null,null,null,null,13,32899.34682667032,401.24033153466883]
[13.5,269.30246596244422,545.13342784332963,0.49401202019084633,null,null,null,null,null,null,null,null,null,null,null,13.5,13926.754320593662,148.42680793139286]
[14,115.44721043915145,364.12044985827333,0.31705774966521927,null,null,null,null,null,null,null,null,null,null,null,14,10176.948716010877,102.35342257703853]
[14.5,29.730098199847518,98.570484190437327,0.30161258153515025,null,null,null,null,null,null,null,null,null,null,null,14.5,3076.4594932620093,29.222221604531089]