University of Oklahoma

Graduate College

modeling and evaluation of constituents of emerging concern through wastewater treatment processes

A thesis

submitted to the Graduate Faculty

in partial fulfillment of the requirements for the

Degree of

Master of Science

By

jason Laubacher

Norman, Oklahoma

2016

modeling and evaluation of constituents of emerging concern through wastewater treatment processes

A thesis approved for the

School of Civil Engineering and Environmental Science

By

______________________________

Dr. Keith Strevett, Chair

______________________________

Dr. David Sabatini

______________________________

Dr. Ellen McDonald

© Copyright by jason laubacher 2016

All Rights Reserved.

To my family and friends who made this possible…

# Acknowledgements

I first want to thank my graduate advisor, Dr. Keith Strevett. Without his intellectual support and input, this research would not be possible. I express my gratitude for his continued guidance and encouragement.

Next, I want to thank the members of my graduate committee, Dr. David Sabatini and Dr. Ellen McDonald. Their input, assistance, and teaching greatly enhanced this research and my academic career.

I wish to thank the many people from Alan Plummer Associates who have invested so much into me and this research. Their academic input and time investment was the basis and source of this research.

Lastly, I want to thank my family and friends who have made my academic career possible. To my parents, I thank you for your continued support in my endeavors, both personally and financially. To my friends and fellow students, I thank you for your personal and academic support.

# Table of Contents

Acknowledgements	iv

Table of Contents	v

List of Tables	viii

List of Figures	x

Abstract	xxi

Chapter 1: Introduction	1

Chapter 2: Literature Review and Background	3

2.1 Removal Efficiencies of CECs in Conventional WWTPs	3

2.2 Removal Efficiencies of CECs in MBRs and Advanced Treatment Processes	5

2.3 Operational Effects on CEC Removal Efficiencies	7

2.4 Removal Mechanisms	10

2.4.1 Sorption	11

2.4.2 Biodegradation	13

2.5 Modeling CECs in GPS-X	15

2.6 NWRF Characteristics	20

Chapter 3: Hypothesis and Objectives	23

3.1 Objective 1	23

3.2 Objective 2	24

3.3 Goal	24

Chapter 4: Methodology	25

4.1 Outline	25

4.2 Base Model Development, Calibration, and Validation	26

4.3 Enhanced Model Development, Calibration, and Validation	27

4.4 Expanded and Advanced Models	32

4.5 Model Limitations	32

Chapter 5: Results and Discussion	34

5.1 Sampling and Analysis	34

5.2 Base Model	45

5.2.1 Base Model Calibration	47

5.2.2 Base Model Validation	50

5.3 Enhanced Model	52

5.3.1 Enhanced Model Calibration and Validation	56

5.4 Expanded Model	65

5.4.1 RAS Analysis	82

5.4.2 Primary Clarifier Volume Analysis	90

5.4.3 Primary Clarifier WAS Analysis	95

5.4.4 Secondary Clarifier WAS Analysis	99

5.5 Advanced Model	106

5.5.1 MBR WAS Analysis	107

5.5.2 MBR RAS Analysis	113

5.6 Expanded and Advanced Model Comparisons	116

Chapter 6: Conclusion	139

References	145

Appendix A: NWRF Typical Wastewater Parameters	151

Appendix B: CECs (and MRLs) Analyzed	170

Appendix C: Stoichiometry Matrix	172

Appendix D: Kinetic Equations	178

Appendix E: Kinetic Parameters	180

# List of Tables

Table 2-1: Typical Removal Percentages of CECs in Conventional WWTPs	4

Table 2-2: Laboratory Tested Conventional Activated Sludge Removal of Pharmaceuticals (Osachoff et al., 2014)	5

Table 2-3: CEC Removal Efficiencies of Various Treatment Processes (Lee et al., 2009)	6

Table 2-4: Calibrated Ibuprofen Partitioning and Biotransformation Coefficients (Ghalajkhani, 2013)	16

Table 2-5: Calibrated Bisphenol-A Partitioning and Biotransformation Coefficients (Ghalajkhani, 2013)	16

Table 2-6: Initial Physical and Chemical Properties of Three Estrogenic Hormones (Monteith et al., 2008)	17

Table 2-7: Current NWRF Layout	20

Table 4-1: NWRF and Base Model Physical Parameters	27

Table 4-2: Indicator CEC Sorption and Biodegradation Constants	30

Table 4-3: Validation CEC Sorption and Biodegradation Constants	31

Table 5-1: Treatment Process Sampling Times	35

Table 5-2: NWRF CEC Removal Percentages	36

Table 5-3: Statistical Analysis of NWRF CEC Removal Percentages	41

Table 5-4: Removal Percentages of Indicator and Validator CECs	44

Table 5-5: Average Influent Conditions for January 2016	44

Table 5-6: Customizable State Variables and Corresponding CECs	53

Table 5-7: Calibrated Biodegradation and Adsorption Constants	57

Table 5-8: Enhanced Model Biodegradation vs. Adsorption during Sampling	65

Table 5-9: Expanded Model Biodegradation vs. Adsorption in the Expanded Model	74

# List of Figures

Figure 2-1: Effluent E1 Percent of Influent based on (a) total HRT (R2=0.39), (b) biological HRT (R2=0.16), and (c) SRT (R2=0.28) (Johnson et al., 2005)	8

Figure 2-2: Ionized CEC Sorption and Biodegradation Diagram	10

Figure 2-3: Sorption Coefficients of Amoxicillin and Ciprofloxacin under varying pH (Githinji et al., 2010)	12

Figure 2-4: Net Specific Growth Rate vs. Substrate Concentration	14

Figure 2-5: Effluent Estrogenic Hormone Concentrations vs. Varying Temperature (Monteith et al., 2008)	18

Figure 2-6: Effluent Estrogenic Hormone Concentrations vs. Aerobic SRT, 20°C (Monteith et al., 2008)	18

Figure 2-7: Effluent Estrogenic Hormone Concentrations vs. Aerobic SRT, 10°C (Monteith et al., 2008)	19

Figure 2-8: Effluent Estrogenic Hormone Concentrations vs. TSS Concentration (Monteith et al., 2008)	19

Figure 2-9: Aerial View of the NWRF	21

Figure 2-10: NWRF Process Flow Diagram	22

Figure 4-1: GPS-X Model Generation Treatment Processes	33

Figure 5-1: NWRF CEC Concentrations with Removal Percentage Greater than 95%	37

Figure 5-2: NWRF CEC Concentrations with Removal Percentage between 90 and 95%	38

Figure 5-3: NWRF CEC Concentrations with Removal Percentage between 70 and 90%	38

Figure 5-4: NWRF CEC Concentrations with Removal Percentage between 50 and 70%	39

Figure 5-5: NWRF CEC Concentrations with Removal Percentage between 30 and 50%	39

Figure 5-6: NWRF CEC Concentrations with Removal Percentage between 0 and 30%	40

Figure 5-7: Indicator and Validator CECs with Removal Percentage Greater than 90%	42

Figure 5-8: Indicator and Validator CECs with Removal Percentage between 30 and 90%	42

Figure 5-9: Indicator and Validator CECs with Removal Percentage between 0 and 30%	43

Figure 5-10: GPS-X Base Model Layout	46

Figure 5-11: 2013 Measured and Modeled Effluent cBOD (RSS=1145.9 and ESS=153.5)	48

Figure 5-12: 2013 Measured and Modeled Effluent TSS (RSS=1724.4 and ESS=613.8)	49

Figure 5-13: 2013 Measured and Modeled Effluent Ammonia (RSS=40.3 and ESS=29.7)	49

Figure 5-14: 2012 Measured and Modeled Effluent cBOD (RSS=1747.7 and ESS =500.1)	51

Figure 5-15: 2012 Measured and Modeled Effluent TSS (RSS=961.4 and ESS =317.7)	51

Figure 5-16: 2012 Measured and Modeled Effluent Ammonia (RSS=69.4 and ESS=40.4)	52

Figure 5-17: Modeled VSS and Xa Concentrations during Sampling	56

Figure 5-18: Enhanced Model Meprobamate Concentrations under Sampling Conditions	58

Figure 5-19: Enhanced Model Triclosan Concentrations under Sampling Conditions	59

Figure 5-20: Enhanced Model Atenolol Concentrations under Sampling Conditions	59

Figure 5-21: Enhanced Model E1 Concentrations under Sampling Conditions	60

Figure 5-22: Enhanced Model Gemfibrozil Concentrations under Sampling Conditions	60

Figure 5-23: Enhanced Model DEET Concentrations under Sampling Conditions	61

Figure 5-24: Enhanced Model Caffeine Concentrations under Sampling Conditions	61

Figure 5-25: Enhanced Model Theobromine Concentrations under Sampling Conditions	62

Figure 5-26: Enhanced Model Sucralose Concentrations under Sampling Conditions	62

Figure 5-27: Enhanced Model Acesulfame-K Concentrations under Sampling Conditions	63

Figure 5-28: Enhanced Model Iopromide Concentrations under Sampling Conditions	63

Figure 5-29: Enhanced Model Iohexol Concentrations under Sampling Conditions	64

Figure 5-30: Expanded Model Meprobamate Concentrations under Sampling Conditions (Modified Flowrate)	66

Figure 5-31: Expanded Model Meprobamate Concentrations under Sampling Conditions (Modified Flowrate)	67

Figure 5-32: Expanded Model Atenolol Concentrations under Sampling Conditions (Modified Flowrate)	67

Figure 5-33: Expanded Model E1 Concentrations under Sampling Conditions (Modified Flowrate)	68

Figure 5-34: Expanded Model Gemfibrozil Concentrations under Sampling Conditions (Modified Flowrate)	68

Figure 5-35: Expanded Model DEET Concentrations under Sampling Conditions (Modified Flowrate)	69

Figure 5-36: Expanded Model Caffeine Concentrations under Sampling Conditions (Modified Flowrate)	69

Figure 5-37: Expanded Model Theobromine Concentrations under Sampling Conditions (Modified Flowrate)	70

Figure 5-38: Expanded Model Sucralose Concentrations under Sampling Conditions (Modified Flowrate)	70

Figure 5-39: Expanded Model Acesulfame-K Concentrations under Sampling Conditions (Modified Flowrate)	71

Figure 5-40: Expanded Model Iopromide Concentrations under Sampling Conditions (Modified Flowrate)	71

Figure 5-41: Expanded Model Iohexol Concentrations under Sampling Conditions (Modified Flowrate)	72

Figure 5-42: Expanded vs. Enhanced Model VSS and Xa Concentrations	73

Figure 5-43: Expanded Extrapolated Meprobamate Concentrations	75

Figure 5-44: Expanded Extrapolated Triclosan Concentrations	75

Figure 5-45: Expanded Extrapolated Atenolol Concentrations	76

Figure 5-46: Expanded Extrapolated E1 Concentrations	76

Figure 5-47: Expanded Extrapolated Gemfibrozil Concentrations	77

Figure 5-48: Expanded Extrapolated DEET Concentrations	77

Figure 5-49: Expanded Extrapolated Caffeine Concentrations	78

Figure 5-50: Expanded Extrapolated Theobromine Concentrations	78

Figure 5-51: Expanded Extrapolated Sucralose Concentrations	79

Figure 5-52: Expanded Extrapolated Acesulfame-K Concentrations	79

Figure 5-53: Expanded Extrapolated Iopromide Concentrations	80

Figure 5-54: Expanded Extrapolated Iohexol Concentrations	80

Figure 5-55: Expanded Model Primary Clarifier and PFR VSS Concentrations	81

Figure 5-56: Expanded Model Primary Clarifier and PFR Xa Concentrations	82

Figure 5-57: Daily Water Temperature	82

Figure 5-58: Primary Clarifier VSS and Xa with Varying RAS	83

Figure 5-59: PFR VSS and Xa with Varying RAS	84

Figure 5-60: Plant Effluent VSS and Xa with Varying RAS	84

Figure 5-61: Primary Clarifier CEC Removal with Varying RAS (0-30% Removal)	85

Figure 5-62: Primary Clarifier CEC Removal with Varying RAS (35-65% Removal)	85

Figure 5-63: Primary Clarifier CEC Removal with Varying RAS (70-100% Removal)	86

Figure 5-64: PFR CEC Removal with Varying RAS (20-40% Removal)	87

Figure 5-65: PFR CEC Removal with Varying RAS (40-60% Removal)	87

Figure 5-66: PFR CEC Removal with Varying RAS (80-100% Removal)	88

Figure 5-67: Plant CEC Removal with Varying RAS (10-50% Removal)	89

Figure 5-68: Plant CEC Removal with Varying RAS (60-100% Removal)	89

Figure 5-69: Plant Effluent TSS, cBOD, and TKN with Varying RAS	90

Figure 5-70: Primary Clarifier VSS and Xa with Varying Primary Clarifier Volume	91

Figure 5-71: PFR VSS and Xa with Varying Primary Clarifier Volume	91

Figure 5-72: Effluent VSS and Xa with Varying Primary Clarifier Volume	92

Figure 5-73: Primary Clarifier CEC Removal with Varying Primary Clarifier Volume	92

Figure 5-74: PFR CEC Removal with Varying Primary Clarifier Volume (33-67% Removal)	93

Figure 5-75: PFR CEC Removal with Varying Primary Clarifier Volume (67-100% Removal)	93

Figure 5-76: Plant CEC Removal with Varying Primary Clarifier Volume (33-67% Removal)	94

Figure 5-77: Plant CEC Removal with Varying Primary Clarifier Volume (67-100% Removal)	95

Figure 5-78: Primary Clarifier VSS and Xa with Varying Primary Clarifier WAS	96

Figure 5-79: PFR VSS and Xa with Varying Primary Clarifier WAS	96

Figure 5-80: Effluent VSS and Xa with Varying Primary Clarifier WAS	97

Figure 5-81: Plant CEC Removal with Varying Primary Clarifier WAS (40-65% Removal)	98

Figure 5-82: Plant CEC Removal with Varying Primary Clarifier WAS (75-100% Removal)	98

Figure 5-83: SRT vs. Secondary Clarifier WAS	99

Figure 5-84: Primary Clarifier VSS and Xa with Varying Secondary Clarifier WAS	100

Figure 5-85: PFR VSS and Xa with Varying Secondary Clarifier WAS	100

Figure 5-86: Effluent VSS and Xa with Varying Secondary Clarifier WAS	101

Figure 5-87: Primary Clarifier CEC Removal with Varying Secondary Clarifier WAS	101

Figure 5-88: PFR CEC Removal with Varying Secondary Clarifier WAS (30-50% Removal)	102

Figure 5-89: PFR CEC Removal with Varying Secondary Clarifier WAS (50-70% Removal)	103

Figure 5-90: PFR CEC Removal with Varying Secondary Clarifier WAS (80-100% Removal)	103

Figure 5-91: Plant CEC Removal with Varying Secondary Clarifier WAS (30-70% Removal)	104

Figure 5-92: Plant CEC Removal with Varying Secondary Clarifier WAS (55-75% Removal)	104

Figure 5-93: Plant CEC Removal with Varying Secondary Clarifier WAS (80-100% Removal)	105

Figure 5-94: Plant Effluent TSS, cBOD, and TKN with Varying Secondary Clarifier WAS	106

Figure 5-95: PFR vs. MBR Effluent, RAS, and WAS in GPS-X	107

Figure 5-96: SRT vs. MBR WAS	108

Figure 5-97: Primary Clarifier VSS and Xa with Varying MBR WAS	108

Figure 5-98: MBR RAS and WAS Streams VSS and Xa with Varying MBR WAS	109

Figure 5-99: MBR Filtrate VSS and Xa with Varying MBR WAS	110

Figure 5-100: Effluent VSS and Xa with Varying MBR WAS	110

Figure 5-101: Primary Clarifier CEC Removal with Varying MBR WAS	111

Figure 5-102: MBR CEC Removal with Varying MBR WAS	111

Figure 5-103: Plant CEC Removal with Varying MBR WAS	112

Figure 5-104: Primary Clarifier VSS and Xa with Varying RAS	113

Figure 5-105: MBR VSS and Xa with Varying RAS	114

Figure 5-106: MBR Filtrate VSS and Xa with Varying RAS	114

Figure 5-107: Effluent VSS and Xa with Varying RAS	115

Figure 5-108: Plant CEC Removal with Varying RAS	115

Figure 5-109: Preliminary and Primary Clarifier Advanced vs. Expanded Xa and VSS under Sampling Conditions (Modified Flowrate)	117

Figure 5-110: MBR or PFR Advanced vs. Expanded Xa and VSS under Sampling Conditions (Modified Flowrate)	118

Figure 5-111: Expanded vs. Advanced Meprobamate under Sampling Conditions (Modified Flowrate)	119

Figure 5-112: Expanded vs. Advanced Triclosan under Sampling Conditions (Modified Flowrate)	120

Figure 5-113: Expanded vs. Advanced Atenolol under Sampling Conditions (Modified Flowrate)	120

Figure 5-114: Expanded vs. Advanced E1 under Sampling Conditions (Modified Flowrate)	121

Figure 5-115: Expanded vs. Advanced Gemfibrozil under Sampling Conditions (Modified Flowrate)	121

Figure 5-116: Expanded vs. Advanced DEET under Sampling Conditions (Modified Flowrate)	122

Figure 5-117: Expanded vs. Advanced Caffeine under Sampling Conditions (Modified Flowrate)	122

Figure 5-118: Expanded vs. Advanced Theobromine under Sampling Conditions (Modified Flowrate)	123

Figure 5-119: Expanded vs. Advanced Sucralose under Sampling Conditions (Modified Flowrate)	123

Figure 5-120: Expanded vs. Advanced Acesulfame-K under Sampling Conditions (Modified Flowrate)	124

Figure 5-121: Expanded vs. Advanced Iopromide under Sampling Conditions (Modified Flowrate)	124

Figure 5-122: Expanded vs. Advanced Iohexol under Sampling Conditions (Modified Flowrate)	125

Figure 5-123: Expanded vs. Advanced Particulate Meprobamate under Sampling Conditions (Modified Flowrate)	126

Figure 5-124: Expanded vs. Advanced Particulate Triclosan under Sampling Conditions (Modified Flowrate)	126

Figure 5-125: Expanded vs. Advanced Particulate Atenolol under Sampling Conditions (Modified Flowrate)	127

Figure 5-126: Expanded vs. Advanced Particulate E1 under Sampling Conditions (Modified Flowrate)	127

Figure 5-127: Expanded vs. Advanced Particulate Gemfibrozil under Sampling Conditions (Modified Flowrate)	128

Figure 5-128: Expanded vs. Advanced Particulate DEET under Sampling Conditions (Modified Flowrate)	128

Figure 5-129: Expanded vs. Advanced Particulate Caffeine under Sampling Conditions (Modified Flowrate)	129

Figure 5-130: Expanded vs. Advanced Particulate Theobromine under Sampling Conditions (Modified Flowrate)	129

Figure 5-131: Expanded vs. Advanced Particulate Sucralose under Sampling Conditions (Modified Flowrate)	130

Figure 5-132: Expanded vs. Advanced Particulate Acesulfame-K under Sampling Conditions (Modified Flowrate)	130

Figure 5-133: Expanded vs. Advanced Particulate Iopromide under Sampling Conditions (Modified Flowrate)	131

Figure 5-134: Expanded vs. Advanced Particulate Iohexol under Sampling Conditions (Modified Flowrate)	131

Figure 5-135: Expanded vs. Advanced Extrapolated Meprobamate	132

Figure 5-136: Expanded vs. Advanced Extrapolated Triclosan	132

Figure 5-137: Expanded vs. Advanced Extrapolated Atenolol	133

Figure 5-138: Expanded vs. Advanced Extrapolated E1	133

Figure 5-139: Expanded vs. Advanced Extrapolated Gemfibrozil	134

Figure 5-140: Expanded vs. Advanced Extrapolated DEET	134

Figure 5-141: Expanded vs. Advanced Extrapolated Caffeine	135

Figure 5-142: Expanded vs. Advanced Extrapolated Theobromine	135

Figure 5-143: Expanded vs. Advanced Extrapolated Sucralose	136

Figure 5-144: Expanded vs. Advanced Extrapolated Acesulfame-K	136

Figure 5-145: Expanded vs. Advanced Extrapolated Iopromide	137

Figure 5-146: Expanded vs. Advanced Extrapolated Iohexol	137

Abstract

Constituents of emerging concern (CECs) have accumulated in drinking water source supply over the past decades. Although there are currently no established treatment standards, CECs should be of concern to the public and the environment. The goal of this study was to better understand the fate of CECs in a conventional activated sludge (CAS) wastewater treatment plant. To achieve this goal, two objectives were identified: (i) evaluate unit operational changes that increase removal efficiency of CECs and (ii) evaluate the efficacy of advanced treatment options. This research measured 98 CECs throughout a CAS facility. Subsequent to these analyses, a stochastic fate model was developed to quantitatively understand CECs’ fate through CAS processes. Results of the model indicate that primary clarifiers and secondary plug flow reactors (PFRs) significantly reduced CEC concentrations. CEC removal percentages in the primary clarifiers range from 9.1% (triclosan) to 79.8% (atenolol). PFR removal percentages range from <0% (meprobamate, gemfibrozil, and sucralose) to >98.6% (caffeine) and overall plant removal percentages range from 6.7% (gemfibrozil) to >98.9% (caffeine). Even with relatively low removal percentages, some influent and effluent CEC concentrations are well below monitoring trigger thresholds, which indicate safe drinking-water concentrations. Furthermore, because wastage rate controls the mean cell residence time, wastage rate is the most influential operational control on the effect on CEC removal. In conclusion, by providing operational and advanced treatment analysis, this modeling approach can help determine key factors in CEC removal from CAS facilities.

# Introduction

Constituents of emerging concern (CECs) are chemicals that are being detected in water that were not previously detected or that are being detected at different levels than anticipated (EPA, 2014). CECs can include household chemicals (detergents, deodorizers), pharmaceuticals (hormones, beta blockers, antibiotics), and personal care products (antacids, caffeine). Because wastewater treatment plant (WWTP) process units are not optimized to remove CECs, these compounds may be discharged into the environment. Accumulation of CECs is a concern for ecosystems, as well as for human consumption via indirect or direct water reuse (Githinji et al., 2010). Several researchers (Bernhard et al., 2006; Clara et al., 2004; Clara at al., 2005; Kimura et al., 2004; Kimura et al., 2007; Radjenović et al., 2007; Wang et al., 2013) have studied the fate of CECs in WWTPs and examined various treatment processes. These treatment processes can include conventional activated sludge (CAS), membrane bioreactors (MBR), reverse osmosis (RO), nanofiltration (NF), aerobic and anaerobic digestion, and advanced oxidation processes (AOPs), including ultraviolet irradiation (UV), hydrogen peroxide (H2O2), and ozone disinfection. Of these treatment processes, CAS is one of the most commonly used. CAS removes CECs using two key removal mechanisms: biological degradation and adsorption to biosolids (Lee et al., 2009). Because removal efficiencies are a function of hydraulic retention time (HRT), solids retention time (SRT), and the physical, chemical and biological characteristics of the wastewater (Johnson et al., 2005; Monteith et al., 2008), CEC concentration levels in wastewater vary greatly and can be difficult to predict. However, various researchers (Lee et al., 2009; Luo et al., 2014; and Miège et al., 2008) have compiled CEC removal efficiency data (Table 2-1) from 153 studies of conventional WWTPs (WWTPs utilizing CAS). As stated above, the primary conclusion among these studies is that CEC removal efficiencies depend upon several factors. However, some common characteristics or commonalities can be observed. For instance, CEC removal percentage increases with increased HRT and SRT (Clara et al., 2005a; Johnson et al., 2005; Monteith et al., 2008). Furthermore, based on the Arrhenius theorem, as temperature increases, CEC removal rates increase (Clara at al., 2004; Monteith et al., 2008). Modeling CECs in a specific WWTP would allow for the evaluation of operational changes to increase CEC removal efficiencies. These changes could include modifications to sludge recycling rates, HRTs, SRTs, biomass makeup and recycling, disinfection processes, and temperature. Finally, because modeling allows for a detailed analysis of the process performance, it provides an indication of what unit processes can be optimized or expanded.

This research will determine key CECs in the City of Norman Water Reclamation Facility (NWRF) and will monitor these CECs in the influent and effluent of major processes within the NWRF. Furthermore, it will develop a stochastic fate model of the NWRF, integrating CECs into the model. More generally, it will help to quantitatively understand CECs through WWTPs and will be a template for further modeling of other WWTPs.

# Literature Review and Background

## Removal Efficiencies of CECs in Conventional WWTPs

There is extensive research on CEC removal efficiencies (Table 2-1) in CAS WWTPs (Lee et al., 2009; Luo et al., 2014; Miège et al., 2008). Although some compounds show similar removal efficiencies from the three studies, other compounds show a wide range due to varying HRT, SRT, and wastewater and biomass makeup. From these studies, it is clear that removal efficiencies are specific to WWTP characteristics and results are quite variable. For instance, removals of acetaminophen, estrone, and ibuprofen do not vary greatly across the three studies. Meanwhile, compounds like bezafibrate, diethyltoluamide (DEET), gemfibrozil, sulfamethoxazole, and tonalide all differ from study to study. Furthermore, Luo et al. (2014) found a large range of removal percentages for some compounds. As mentioned, these ranges in removal percentages are attributed to variability of HRT, SRT, and wastewater and biomass makeup.

Table 2-1: Typical Removal Percentages of CECs in Conventional WWTPs

|  | Removal Percentage |  |  |  | Removal Percentage |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Compound | Luo et al., 2014 | Lee et al., 2009 | Miège et al., 2008 | Compound | Luo et al., 2014 | Lee et al., 2009 | Miège et al., 2008 |
| 17α-Ethynylestradiol | 43.8–100 |  | ~79 | Estrone | 74.8–90.6 |  | ~76 |
| Acetaminophen | 98.7–100 | 98.4 |  | Galaxolide | 87.8 | ~60-95 | ~61 |
| Alkylphenol |  | ~30-95 |  | Gemﬁbrozil | <0–92.3 | 38.8 | ~61 |
| Alkylphenol ethoxylate |  | ~75-95 |  | Glibenclamide |  | 44.5 |  |
| Atenolol | <0–85.1 | 0 | 0 | Hydrochlorothiazide |  | 76.3 |  |
| Atrazine | <0–25 |  |  | Ibuprofen | 72–100 | 82.5-~98 | ~78 |
| Bayrepel acid |  |  |  | Indomethacin |  | 23.4 |  |
| Bentazone |  |  |  | Ketoprofen | 10.8–100 | 51.5-~55 | ~52 |
| Benzophenone-3 | 63.8–98.2 |  |  | MCPP |  | 13 |  |
| Bezaﬁbrate | 9.10–70.5 | ~40-98 | ~70 | Mefenamic acid | <0–70.2 | 29.4-~70 | ~25 |
| Bisphenol-A | 62.5–99.6 | 91 |  | Metoprolol | 3–56.4 | 0 | ~30 |
| Caffeine | 49.9–99.6 |  |  | Naproxen | 43.3–98.6 | ~65-85.1 | ~74 |
| Carbamazepine | <0–62.3 | 0-7 | ~8 | Nonylphenol | 21.7–99 |  |  |
| Cloﬁbric acid | <0–93.6 | 27.7-~50 | ~25 | Octylphenol | <0–96.7 |  |  |
| Clotrimazole | 84.5–93.6 |  |  | Ofloxacin |  | 23.8 |  |
| DBP | 73.6–75.5 |  |  | Paroxetine |  | 90.6 |  |
| DEET | 65.6–79.5 | 17 |  | Pravastatin |  | 61.8 |  |
| DEHP | 25–97 |  |  | Propyphenazone |  | 42.7 | 0 |
| Diazinon | <0 |  |  | Rantidine |  | 42.2 |  |
| Diclofenac | <0–81.4 | ~24-50.1 | ~35 | Salicylic acid | 89.6–100 |  | ~99 |
| Diuron | 26.7–71.9 |  |  | Sulfamethoxazole | 4–88.9 | 55.6 | ~60 |
| DMP | 84.8–93.5 |  |  | TCEP | <0 | 30 |  |
| EDTA |  | 1 |  | TCPP | <0 | 13 |  |
| Enrofloxacin |  |  |  | Tebuconazole | <0–58.7 |  |  |
| Erythromycin | <0–82.5 | 23.8 |  | Tonalide | 84.7 | ~50-97 | ~64 |
| Estradiol | 92.6–100 |  |  | Triclosan | 71.3–99.2 |  | ~84 |
| Estriol | 100 |  |  | Trimethoprim | <0–81.6 |  | ~43 |

Osachoff et al. (2014), using synthetic wastewater containing pharmaceutical and personal care products, studied removal efficiencies (Table 2-2) in a bench-scale CAS process. The synthetic wastewater contained: caffeine, di(2-ethylhexyl)phthalate, estrone, 17α-ethinylestradiol, ibuprofen, naproxen, 4-nonlyphenol, tonalide, triclocarbon, and triclosan.

Table 2-2: Laboratory Tested Conventional Activated Sludge Removal of Pharmaceuticals (Osachoff et al., 2014)

| Pharmaceutical | Influent Concentration (ng/L) | Effluent Concentration (ng/L) | Percent Removed |
| --- | --- | --- | --- |
| Caffeine | 45,579 | 250 | 99.5 |
| Di(2-ethylhexyl)phthalate | 40,609 | 15,565 | 61.7 |
| Estrone | 70 | 20 | 71.6 |
| 17α-Ethinylestradiol | 6.0 | 1.5 | 75.1 |
| Ibuprofen | 27,600 | 8667 | 68.6 |
| Naproxen | 15,000 | 9000 | 40.0 |
| 4-Nonylphenol | 31,000 | 125 | 99.6 |
| Tonalide | 1017 | 25 | 97.5 |
| Triclocarbon | 3000 | 73 | 97.6 |
| Triclosan | 3000 | 250 | 91.7 |

Di(2-ethylhexyl)phthalate, estrone, 17α-Ethinylestradiol, and ibuprofen were only moderately removed while naproxen was moderately conserved in the treatment process. Because of their lower removal efficiencies, di(2-ethylhexyl)phthalate, estrone, 17α-Ethinylestradiol, ibuprofen, and naproxen should be noted as potential key CECs for modeling.

## Removal Efficiencies of CECs in MBRs and Advanced Treatment Processes

In addition to compiling data for CAS, Lee et al. (2009) accumulated and analyzed CEC removal efficiencies from MBR, NF, RO, granular activated carbon (GAC), and powdered activated carbon (PAC). MBRs use CAS but replace the secondary clarifier with membrane filtration. NF, RO, GAC, and PAC are considered advanced treatment (AT) processes and are typically used after WWTP processes like CAS or MBRs. NF and RO use membranes to filter contaminants from the passing wastewater. GAC uses adsorption in a fixed-bed process. In contrast, PAC is a suspended media in the water. All of these advanced treatment (AT) processes performed better than CAS in removing CECs (Lee et al., 2009). Table 2-3 shows removal efficiency characteristics of several AT processes.

Table 2-3: CEC Removal Efficiencies of Various Treatment Processes (Lee et al., 2009)

| Process | Compounds Studied | Percent of Compounds with No Removal | Percent of Compounds with Removal Below 50% | Percent of Compounds with Removal Above 90% or Below Detection Limit |
| --- | --- | --- | --- | --- |
| MBR | 49 | 14 | 33 | 39 |
| CAS | 33 | 9 | 64 | 27 |
| NF | 57 | n.d. | 17 | 82 |
| RO | 60 | n.d. | 12 | 82 |
| GAC | 29 | 0 | 0 | 97 |
| PAC | 71 | 6 | 31 | 41 |

n.d. not determined

Although GAC does have high removal efficiencies, according to Lee et al. (2009), several studies found that competitive adsorption can decrease removal efficiency and the operating life of the filter, especially when organic matter is present (Lee et al., 2009). Competitive adsorption is a process in which compounds compete for adsorption sites on cells. It is controlled by the maximum heat and energy required for adsorption (Gun’ko, 2007). Because of this phenomenon, hydrophilic and large-molecular weight compounds may not be removed as well because they do not have accessibility to the inner pores of carbon in the filter (Lee et al., 2009).

GAC can be combined with a biologically active layer in what is referred to as biological activated carbon (BAC). Reungoat et al. (2011) found that BAC had removal efficiencies of greater than 90% for 21 pharmaceuticals analyzed. Although adsorption might have some role in these high removal percentages, biodegradation was found to be the primary removal mechanism (Reungoat et al., 2011).

## Operational Effects on CEC Removal Efficiencies

Several researchers have examined the effects of WWTP operational parameters on CEC removal efficiencies (Johnson et al., 2005; Clara et al., 2005a; Lishman et al., 2006). Johnson et al. (2005) studied the impact that HRT, SRT, biological HRT (HRT in the biological treatment zones), and temperature have on the estrogenic hormone estrone (E1). In analyzing seventeen WWTPs throughout Europe; Johnson et al. (2005) found that E1 removal rates (Figure 2-1) increased as HRT and SRT increased, especially biological HRT. It should be noted that the Pearson product-moment correlation coefficient (R2), obtained from a linear regression of each parameter, is relatively low. Consequently, there exists a general downward trend (Figure 2-1) from these data but resulting relationships should not be viewed as exact tendencies. It is important to note that the influent concentrations were estimated from excretion rates, population data, and flow, resulting in artificially higher E1 levels at low retention times (Figure 2-1). Temperature did not have a significant effect on E1 removal efficiency.

Figure 2-1: Effluent E1 Percent of Influent based on (a) total HRT (R2=0.39), (b) biological HRT (R2=0.16), and (c) SRT (R2=0.28) (Johnson et al., 2005)

Clara et al. (2005a) analyzed E1, 17β-estradiol (E2), 17α-ethinylestradiol (EE2), caffeine, and bezafibrate using bench-scale experiments with varying SRTs along with sampling at five different WWTPs. The study concluded that the critical SRT (the SRT for which the compound removal is maximized) for E1 and E2 was between 5 and 10 days, with almost complete removal of these two compounds occurring after 10 days. EE2, meanwhile, did not show consistent removal rates. Even for similar SRTs, removal rates varied quite drastically (Clara et al., 2005a). Both E1 and E2 are natural estrogens, while EE2 is a pharmaceutical. This could be the reason for variation in removal through WWTPs. Both caffeine and bezafibrate had removal rates of more than 95%. Furthermore, critical SRTs for caffeine and bezafibrate were found to be 5 and 10 days, respectively (Clara et al., 2005a).

Lishman et al. (2006) analyzed CECs in twelve different WWTPs along the Thames River in Canada. Seven of the twelve WWTPs consisted of only CAS while two of the twelve had CAS and media filtration. The remaining treatment plants used lagoon treatment processes. Among other CECs, Lishman et al. (2006) evaluated concentrations of gemﬁbrozil, diclofenac, celestolide, phantolide, galaxolide, and tonalide. As expected, gemfibrozil, diclofenac, and celestolide (ADBI) all had increased removal efficiencies as SRT increased. Traseolide (ATII), galaxolide (HHCB), and tonalide (AHTN), meanwhile, did not show these tendencies. For a SRT between 3 and 5 days, no correlation was discovered. However, for SRT over 5 days, ATII removal efficiency increased with increasing SRT. Meanwhile, for HHCB and AHTN, removal efficiency seemed to slightly decrease with increased SRT. This can likely be attributed to the lack of data for larger SRT ranges. In many cases, effluent concentrations of these compounds were below detectable levels (BDL), making it difficult to correlate any patterns in removal efficiency. Other CECs evaluated, including ibuprofen and naproxen, had high (~95%) removal efficiencies but also varied with increased SRT. For these two compounds, Lishman et al. (2006) noted that removal efficiency tendencies could not be found with treatment configurations or operational parameters.

## Removal Mechanisms

CECs are removed from wastewater by biodegradation and adsorption to biosolids (Lee et al., 2009; Ghalajkhani, 2013). Although volatilization could be considered, it is negligible for most CECs due to their low octanol-water partitioning coefficients (log KOW) and Henry coefficients (KH) (Clara et al., 2005b). CEC compounds can partition between the neutral (HA) and ionized form (A-) which impact the rate of sorption or biodegradation (Figure 2-2).

Figure 2-2: Ionized CEC Sorption and Biodegradation Diagram

As presented in Figure 2-2, sorption and biodegradation of ionized CECs must be accounted for in the neutral and ionized forms. In contrast, neutral compounds (not shown) only require sorption and biodegradation rates for the neutral form. However, for this research, it is unknown whether each CEC is in the ionized or neutral form. Therefore, sorption and biodegradation rates are considered to be equal for both forms.

### Sorption

Sorption consists of both adsorption from liquid to a solid and desorption, or a solid to liquid phase. The amount of a compound sorbed onto biomass can be modeled by the compound’s partitioning coefficient, Kd (Equation 2.1) (Joss et al., 2006). Note: Ms is mass associated with substrate, Mss is mass associated with suspended solids, Mx is mass associated with biomass, L is a unit of length, and T is a unit of time.

| Kd=XVSS×S | Equation 2.1 |
| --- | --- |

where

Kd is the compound partitioning coefficient (L3/Mss)

X is the sorbed compound concentration (Ms/L3)

S is the concentration of the compound (Ms/L3), and

VSS is the volatile suspended solids concentration in the reactor (Mss/L3)

Rearranged, the amount of sorbed compound is:

| X=Kd×VSS×S | Equation 2.2 |
| --- | --- |

As shown, sorption is not modeled using a kinetic expression. However, Ternes et al., (2004) found that equilibrium was reached after just 0.5 hours in a batch reactor. Because the clarifiers and the PFR at the NWRF have HRTs greater than 0.5 hours, sorption is assumed to reach equilibrium.

The desorption rate (rdes (Ms/L3)) does not depend on the influent concentration of the compound. Instead, it is dependent on the concentration of the compound on the biomass. Therefore, rdes (Equation 2.3) is equal to Kdes multiplied by the concentration of the compound sorbed onto the biomass (X) (Ghalajkhani, 2013).

| rdes=KdesX | Equation 2.3 |
| --- | --- |

The rate of desorption is assumed to be slower than adsorption. Therefore, kdes is assumed to be 0.1 d-1, meaning that desorption is assumed to happen at 10% of the rate that adsorption takes place (Ghalajkhani, 2013).

Githinji et al. (2010) analyzed ciprofloxacin and amoxicillin, determining sorption rates and biodegradation tendencies. The experimental sorption rates determined are presented in Figure 2-3.

Figure 2-3: Sorption Coefficients of Amoxicillin and Ciprofloxacin under varying pH (Githinji et al., 2010)

The key conclusion developed from this study is that ciprofloxacin had higher adsorption rates than amoxicillin and amoxicillin portioning coefficients decreased with increasing values of pH. Ciprofloxacin partitioning coefficients reached a maximum at a pH of 5.5 and decreased as pH increased after that point. Because amoxicillin has a higher pKa value than ciprofloxacin, it dissociates in water at a higher rate. Therefore, amoxicillin has less electrostatic attraction and sorbs to solids at a lower rate than ciprofloxacin (Githinji et al., 2010). At higher pH, amoxicillin and ciprofloxacin compounds are more negatively charged, resulting in less electrostatic attraction with solids in the system. Consequently, the sorption potential of these compounds decreases at higher pH values (Githinji et al., 2010). This should be considered when selecting sorption coefficients for CECs. Furthermore, neither antibiotic significantly degraded within 48 hours, indicating the importance of an adsorption removal mechanism (Githinji et al., 2010).

### Biodegradation

Lee et al. (2012) used a Monod biokinetic expression to model triclosan degradation in wastewater. The same concept can be used for other CECs with the alteration of half saturation constants (K) and maximum specific rate of substrate utilization (q̂). The Monod expression, in terms of substrate utilization (rut), is presented in Equation 2.4 (Rittmann and McCarty, 2001).

| rut=-qSK+SXa | Equation 2.4 |
| --- | --- |

where

rut is the rate of substrate utilization (Ms/L3 · T)

q̂ is the maximum specific rate of substrate utilization (Ms/Mx · T)

S is the concentration of the rate-limiting substrate (Ms/L3)

K is the half-saturation coefficient of the substrate (Ms/L3), and

Xa is the active biomass concentration (Mx/L3)

It should be noted that this is a pseudo-order utilization rate, resulting in two boundary conditions. At low concentrations of substrate (S<<K, which is the case for CECs), the net specific growth rate (µ) can be modeled as a first-order rate (Figure 2-4).

Figure 2-4: Net Specific Growth Rate vs. Substrate Concentration

Based on the observation that the CEC exists at low concentrations in the waste stream, it can be assumed that first-order rates apply to CEC biodegradation. Therefore, the net rate of biomass growth, rnet, can be defined by Equation 2.5.

| rnet=YqSK+SXa-bXa | Equation 2.5 |
| --- | --- |

where

rnet is the net rate of active biomass growth (Mx/L3 · T)

Y is the true yield (Mx/Ms), and

b is the endogenous-decay coefficient (1/T)

Because half-saturation coefficients are not well documented, a simpler modeling method for biodegradation is to use biodegradation constants. As noted, because first-order rates apply, Equation 2.6 can be used in determining removal due to biodegradation (Joss et al., 2006; Tran et al., 2015).

| rut=-kbioXaS | Equation 2.6 |
| --- | --- |

where

kbio is the biodegradation constant (L3/Mx · T)

Similar to Equation 2.5, rnet can then be described using Equation 2.7.

| rnet=YkbioXaS-bXa | Equation 2.7 |
| --- | --- |

However, because CEC concentrations are small compared to biomass concentrations, their effect on biomass can be considered negligible. For this reason and to simplify modeling, the net rate of biomass growth was modeled as the negative rate of CEC utilization (Equation 2.6).

## Modeling CECs in GPS-X

Based on a thorough literature review, much of the CEC research focus has been centered around bench/pilot scale studies; with little attention aimed at treatment process optimization. However, Ghalajkhani (2013); Monteith et al. (2008) and Schraa et al. (2006), have provided a framework for using a standard process model (GPS-X, Hydromantis, Ontario Canada) to study CEC fate in municipal wastewater systems. CECs were integrated into the models using the Model Developer (MD) tool. MD allows for the creation of new models using a matrix format. New models allow for the addition of rates and kinetic and stoichiometric relationships, as well as other model parameters (Hydromantis, 2014).

Ghalajkhani (2013) used GPS-X to model the fate of xenobiotic organic compounds (XOCs). XOCs stem from personal care products, pharmaceuticals, excreted hormones, and household and industrial chemicals. Using data from existing research for calibration (Collado et al., 2012; Zhao et al., 2007), the following sorption and biotransformation constants were determined for ibuprofen (Table 2-4) and bisphenol-A (Table 2-5). Kd-HA is the solid-liquid partitioning coefficient for the neutral form of an iodized compound; Kd-A- is the solid-liquid partitioning coefficient for the ionized form of an ionized compound; Kd-N is the solid-liquid partitioning coefficient for a neutral compound; Kbio-HA is the aerobic biodegradation rate constant for the neutral form of an ionized compound; and Kbio-N is the aerobic biodegradation rate constant for a neutral compound (Ghalajkhani, 2013).

Table 2-4: Calibrated Ibuprofen Partitioning and Biotransformation Coefficients (Ghalajkhani, 2013)

| Parameter | Lower Bound | Upper Bound | Optimal Value ± Standard Error |
| --- | --- | --- | --- |
| Kd-HA (L/mg biomass) | 1.59E-05 | 7.53E-04 | 3.23E-4±6.02E-5 |
| Kbio-HA (L/mg biomass/d) | 0.0681 | 0.2877 | 0.1943±0.10 |
| Kd-A- (L/mg biomass) | 1.32E-06 | 6.26E-05 | 1.96E-5±5.72E-6 |

Note: The biodegradation rate for the ionized form of an ionized compound, Kbio-A-, was not provided.

Table 2-5: Calibrated Bisphenol-A Partitioning and Biotransformation Coefficients (Ghalajkhani, 2013)

| Parameter | Lower Bound | Upper Bound | Optimal Value ± Standard Error |
| --- | --- | --- | --- |
| Kd-N (L/mg biomass) | 5.75E-05 | 7.19E-04 | 4.935E-4±5.3E-5 |
| Kbio-N (L/mg biomass/d) | 0.0047 | 0.0697 | 0.0502±7.9E-3 |

Rate constants similar to those shown in Table 2-4 and Table 2-5 will be needed in order to model other CECs. Once CECs are selected for modeling, biodegradation constants and partitioning coefficients will be estimated from literature values.

Monteith et al. (2008) developed equations for sorption and biotransformation processes (including parent and daughter cells) of the estrogenic hormones E1, E2, and synthetic estrogen EE2. These equations were developed via literature review and the results were compared with actual field data in order to calibrate the model. Table 2-6 presents the initial and calibrated physical and chemical properties that Monteith et al. (2008) used in modeling. The calibrated initial properties were adjusted after comparing the modeled results to literature data (Monteith et al., 2008).

Table 2-6: Initial Physical and Chemical Properties of Three Estrogenic Hormones (Monteith et al., 2008)

| Property | E1 | E2 | EE2 |
| --- | --- | --- | --- |
| Molecular weight (Daltons) | 270.4 | 272.4 | 296.4 |
| Density (g/cm3) | 1.23 | 1.2 | 1.2 |
| Henry's coefficient (Lliq/Lgas) | 1.54E-08 | 1.47E-10 | 3.21E-10 |
| Log Kow | 3.13 | 4.01 | 3.67 |
| Initial Aerobic kbio (m3/g VSS-d) | 0.205 | 0.429 | 0.00097 |
| Initial Anoxic kbio (m3/g VSS-d) |  | 0.125 |  |
| Initial Anaerobic kbio (m3/g VSS-d) |  | 0.222 |  |
| Calibrated Aerobic kbio (m3/g VSS-d) | 0.0216 | 0.024 | 0.00097 |
| Calibrated Anoxic kbio (m3/g VSS-d) |  | 0.007 |  |
| Calibrated Anaerobic kbio (m3/g VSS-d) |  | 0.013 |  |

After calibration, the model was analyzed with varying temperature, SRT, HRT, and total suspended solids (TSS) concentrations. Under 9 to 11°C, sorption impacts removal rates more than biotransformation. At these low temperatures, biotransformation kinetics decrease, and the compounds are removed primarily from sorption to biosolids. However, above 9 to 11 °C, it was found that biotransformation plays a larger role on the removal of the hormones (Monteith et al., 2008). Generally, as temperature increases, so does the removal of the estrogenic hormones (Figure 2-5).  This is likely due to the Arrhenius equation, which states that kinetic constants increase as temperature increases.

Figure 2-5: Effluent Estrogenic Hormone Concentrations vs. Varying Temperature (Monteith et al., 2008)

Monteith et al. (2008) also studied isothermal SRT impact on hormone concentrations. At 20°C, no significant changes in effluent concentration were observed after an aerobic SRT of 5 days (Figure 2-6). However, at a constant temperature of 10°C, E2 concentrations decreased as aerobic SRT increased (Figure 2-7). E1 and EE2 decreased, but not substantially.

Figure 2-6: Effluent Estrogenic Hormone Concentrations vs. Aerobic SRT, 20°C (Monteith et al., 2008)

Figure 2-7: Effluent Estrogenic Hormone Concentrations vs. Aerobic SRT, 10°C (Monteith et al., 2008)

The effects of aeration HRT were examined on the estrogenic hormone levels. As expected, increased aeration HRT resulted in decreased levels of total hormone concentrations. In this case, removal efficiency plateaued after a HRT of about five days.

Monteith et al. (2008) also examined the effect that TSS concentrations have on the hormone concentrations. Because the majority of the estrogenic hormones in the primary and final effluents were free and not bound, TSS did not have a large effect on the hormone concentrations (Figure 2-8).

Figure 2-8: Effluent Estrogenic Hormone Concentrations vs. TSS Concentration (Monteith et al., 2008)

Schraa et al. (2006) modeled pharmaceutical wastewater through a WWTP that contained fungal and bacterial integrated fixed-film activated sludge (IFAS). Schraa et al. (2006) used the mantis model, a modified activated sludge model (ASM), because of the following modifications from ASM: temperature dependence of kinetic parameters; growth limitation due to low ammonia conditions; simultaneous nitrification and denitrification; and updated kinetic parameters. After calibration, modeling was used to analyze the WWTP with treatment processes offline, varying temperatures, and lower air flowrates in the reactors (Schraa et al., 2006).

## NWRF Characteristics

The NWRF has an average flowrate of about 10 MGD (from 2012 and 2013 data). Utilizing CAS, it consists of primary and secondary clarification, a plug flow reactor (PFR) aeration basin, and anaerobic digesters. The current unit processes and sizes are shown in Table 2-7. Figure 2-9 and Figure 2-10 display a labeled aerial view and a process flow diagram with sampling locations, respectively.

Table 2-7: Current NWRF Layout

2015 NWRF Layout

Bar Screen

2 Grit Chambers

2 Primary Clarifiers @ 0.200 MG each 2 Primary Clarifiers @ 0.288 MG each

3 Chamber Aeration Basin @ 0.990 MG per chamber

2 Secondary Clarifiers @ 0.676 MG each 2 Secondary Clarifiers @ 1.33 MG each

4 Gravity Thickeners @ 0.019 MG each

4 Anaerobic Digesters @ 0.633 MG each

Figure 2-9: Aerial View of the NWRF

Figure 2-10: NWRF Process Flow Diagram

# Hypothesis and Objectives

It is hypothesized that utilizing MBRs will be more effective than operational changes to the CAS process at removing CECs in the NWRF. From literature, MBRs typically have higher removal efficiencies than CAS (Lee et al., 2009). MBRs are desirable because of their small space requirements, their capability of replacing secondary clarifiers (EPA, 2007), and their ability to be placed inside or outside an existing CAS aeration basin (Lee et al., 2009). Furthermore, because MBRs are able to maintain higher concentrations of biomass, less volume is needed in CAS aeration basins (EPA, 2007). Finally, MBRs provide additional pathogen barriers, providing increased removal that may be desirable for water reuse applications (Alan Plummer Associates, Incorporated, 2015).

## Objective 1

The first objective of this research is to evaluate the impact of operational parameters (HRT, SRT, sludge recycling, disinfection adjustments, etc.) on the removal efficiency of CECs. To achieve this objective the following tasks have been identified: (i) develop a model of the current NWRF layout (base model), (ii) calibrate the base model, (iii) validate the base model, (iv) integrate CECs using MD to develop an enhanced model, (v) calibrate the enhanced model, and (vi) validate the enhanced model.

## Objective 2

The second objective is to evaluate AT options (such as MBR, NF, RO, UV disinfection, GAC, and BAC) that help to increase removal efficiency of CECs. This objective will use the advanced model to further the understanding of the fate through AT processes.

## Goal

The goal of this research is to develop a stochastic model to optimize CEC removal efficiencies and operations at the NWRF.

# Methodology

The scope of this research included: reviewing literature regarding the fate of CECs through WWTPs; analyzing water quality data of the influent and effluent of major treatment processes from the NWRF; determining rate constants and biological and physiochemical properties of CECs to be modeled; developing a base model in GPS-X of the current layout of the NWRF; calibrating and validating the base model; developing an enhanced model that uses MD to integrate CECs into the base model; calibrating and validating the enhanced model; developing an expanded model that expands the enhanced model to include the future layout of the NWRF; and developing an advanced model to evaluate operational changes and AT options to increase removal efficiencies of CECs.

## Outline

The first step of this research was to complete a thorough literature review. Common CECs in wastewater and typical removal efficiencies were determined. Due to the vast numbers of CECs that could be used and due to budget limitations, indicator CECs were modeled. In order to select CECs for modeling, CECs with similar physiochemical and biological characteristics and function were grouped together. After grouping, indicator CECs were used to represent the group. Although validators did not always behave the same as indicators, most validators performed the same as its indicator CEC through at least one treatment process (Table 5-4). Therefore, indicators from a resource document by Alan Plummer Associates, Incorporated (2015) were used for modeling in order to better understand entire groups of CECs. The sampling locations at the NWRF were the preliminary treatment effluent, primary clarifier effluent, aeration basin effluent, secondary (final) clarifier effluent, primary anaerobic digester effluent, and secondary anaerobic digester effluent. After selection of CECs, literature values were again used to determine biodegradation constants and partitioning coefficients of CEC (Table 4-2).

## Base Model Development, Calibration, and Validation

During CEC literature review and selection, the base NWRF model was developed. Due to limitations of the GPS-X model, only half of the plant was modeled. Because the NWRF has four primary, four secondary clarifiers, four thickeners, and four anaerobic digesters (as of 2015), only two of each of these treatment processes were modeled. The PFR’s volume, meanwhile, was divided by two and all three chambers were kept for modeling purposes. Furthermore, because only one-half of the plant was modeled, the influent flowrate was divided by two. Because the flow was halved, one of each size of clarifier (both primary and secondary) was used for modeling. In the model, flow was further split to account for the size of each clarifier. These splits, along with the current NWRF and modeled physical parameters are shown in Table 4-1.

Table 4-1: NWRF and Base Model Physical Parameters

| 2015 NWRF Layout | Base and Enhanced Model Layout |
| --- | --- |
| Bar Screen | Bar Screen |
| 2 Grit Chambers | 1 Grit Chamber |
| 2 Primary Clarifiers @ 0.200 MG each 2 Primary Clarifiers @ 0.288 MG each | 1 Primary Clarifier @ 0.200 MG (40% of flow) 1 Primary Clarifier @ 0.288 MG (60% of flow) |
| 3 Chamber Aeration Basin @ 0.990 MG per chamber | 3 Chamber Aeration Basin @ 0.495 MG per chamber |
| 2 Secondary Clarifiers @ 0.676 MG each 2 Secondary Clarifiers @ 1.33 MG each | 1 Secondary Clarifier @ 0.676 MG (34% of flow) 1 Secondary Clarifier @ 1.33 MG (66% of flow) |
| 4 Gravity Thickeners @ 0.019 MG each | 2 Gravity Thickeners @ 0.019 MG each |
| 4 Anaerobic Digesters @ 0.633 MG each | 2 Anaerobic Digesters @ 0.633 MG each |

Splitting the plant allowed for the model to be calibrated using the data provided by the NWRF. The data provided by the NWRF included typical WWTP parameters, including: temperature, carbonaceous biological oxygen demand (cBOD), ammonia, TSS, dissolved oxygen (DO), alkalinity, and pH from 2012 and 2013 (Appendix A: NWRF Typical Wastewater Parameters).

Calibration involved adjustment of model parameters so that modeled effluent concentration levels of cBOD, ammonia, and TSS closely match actual levels found from sampling over the entire year of 2013. The model was then validated by confirming the effluent concentrations of cBOD, ammonia, and TSS from 2012. Validation confirms the calibration of the system, verifying that modeled effluent concentrations match data from the NWRF. With validation, the effluent data should closely match the levels from the model.

## Enhanced Model Development, Calibration, and Validation

The next step was to integrate CECs into the base model using the MD tool. The MD tool allows custom libraries to be created within GPS-X. MD uses a matrix format and can be used to add new contaminant parameters and alter rate equations and constants, making it possible to precisely model varying wastewater parameters. In this case, CEC parameters were added to the base model, creating the enhanced model. During this process, the five sections of the MD tool were populated. These sections are: GPS-X Libraries, Stoichiometric Matrix, Model Kinetics, Model Parameters, and Composite Variables. The GPS-X Libraries section contains the existing state variables and composite variable stoichiometry parameters. State variables are used by GPS-X to perform mass balance calculations. They include the various forms of COD, nitrogen, phosphorus, and other wastewater parameters. Composite variables are calculated from the state variables and include: TSS, volatile suspended solids (VSS), total cBOD5, total COD, total Kjeldahl nitrogen (TKN), TN, total phosphorus, and total carbon. The Stoichiometric Matrix contains state variables in columns and kinetic processes in rows, showing the stoichiometric relationship between the state variables and the rate processes within the model. It allows the addition of process rates such as the sorption, desorption, and biodegradation of CECs. The Model Kinetics section has the kinetic equations used in the model. It incorporated Equation 2.2 to Equation 2.6 to quantify CEC sorption, desorption, biodegradation, and biomass production from CEC biodegradation, respectively. The Model Parameters tab contains state variables, stoichiometric parameters, and kinetic parameters. This section allows for the entry of new rate constants and is where desorption constants, partitioning coefficients, and biodegradation constants were entered into the model. The Model Parameters section also allows for the application of Arrhenius coefficients, making it possible to analyze temperature’s effect on CEC removal. Finally, the Composite Variables tab shows fixed composite variable stoichiometry (Hydromantis, 2014).

After CECs were integrated, the enhanced model was calibrated and validated in a similar way to the base model. In this case, indicator CECs from certain groups (Alan Plummer Associates, Incorporated, 2015) were selected for calibration (Table 4-2), while other CECs from the same group were used for validation (Table 4-3). Along with compiling a list of indicator CECs, Alan Plummer Associates (2015) also compiled monitoring trigger thresholds (MTTs) for each CEC. These MTTs assume a 150-pound person that consumes 2 liters of water per day to estimate acceptable concentrations of CECs based on tolerable daily intake values (Alan Plummer Associates, Incorporated, 2015).

Table 4-2: Indicator CEC Sorption and Biodegradation Constants

| Indicator CEC | Class | MTT (ng/L) | Kd (L/kg) | kbio (L/g – d) | Validation CEC |
| --- | --- | --- | --- | --- | --- |
| 17β-Estradiol (E2) | Hormone | <1 | 426-2003a 461±212f | 350±42j (Aerobic) 460±60j (Anoxic) 175±10j (Anaerobic) | Estrone (E1) |
| Atenolol | Beta Blocker | 4,000 | 0.21d 64±88e 17-97g | 0.69g 1.1±0.1-1.9±0.2l | Lopressor |
| TCEP | Flame Retardant | 5,000 | <30-162±72k ┼ | ┼ | TCPP |
| Caffeine | Stimulant | - | 199.5-794.3i | 39.6-50.9n | Theobromine (Caffeine degradate) |
| Gemfibrozil | Lipid Regulator | 800,000 | 75-1106a 19.3±9.3e 47.9-275.4h | 6.4-9.6c | Bezafibrate |
| Iopromide | X-Ray Contrast Agent | 750,000 | 11±1b 6.9f | 1.6-2.5c | Iohexol |
| Meprobamate | Anti-Anxiety | 200,000 | 316.2-631.0i | - | Diazepam |
| DEET | Repellant | 200,000 | 58.9-128.8h 63.1-1258.9i | - | N/A* |
| Primidone | Anti Convulsant | 10,000 | <30-45±10k 7±1l | <0.1l | N/A* |
| Sucralose | Sugar Substitute | 150,000,000 | 95.5±28.9-761.1±323.5m | 0.003-0.009m | Acesulfame-K |
| Triclosan | Antibacterial | 2,100,000 | 1905-9550h | 1.2-3.6n | Triclocarban |

* Note: Validation CECs that are similar to the indicator CEC do not exist in the sampling suite.

┼  Note: Several studies have shown zero removal of CEC (Luo et al., 2014; Meyer and Bester, 2004)

Note: Concentrations were below MRL during analysis

Table 4-3: Validation CEC Sorption and Biodegradation Constants

| Class | Validation CEC | Kd (L/kg) | kbio (L/g – d) |
| --- | --- | --- | --- |
| Hormone | Estrone (E1) | 170-365a 303±59f | 162±25j (Aerobic) 30±10j (Anoxic) 10±1 j (Anaerobic) |
| Beta Blocker | Lopressor | 7-19g | 0.58g |
| Flame Retardant | TCPP | ┼ | ┼ |
| Caffeine Degradate | Theobromine | ^ | ^ |
| Lipid Regulator | Bezafibrate | 158.5-501.2i | 2.1-3.0c |
| X-Ray Contrast Agent | Iohexol | - | 1.8-2.4c |
| Anti-Anxiety | Diazepam | 21±8-44±26b 81.3-295.1h | 0.035c <0.016l |
| Sugar Substitute | Acesulfame-K | 47.5±4.5-365.9±338.4m | 0.0448-0.0594m |
| Antibacterial | Triclocarban | 25703h |  |

* Note: Validation CECs that are similar to the indicator CEC do not exist in the sampling suite.

┼  Note: Several studies have shown zero removal of CEC (Luo et al., 2014; Meyer and Bester, 2004)

Note: Concentrations were below MRL

^ Literature data not found. Values are assumed to be similar to caffeine constants.

a Urase and Kikuta, 2005

b Ternes et al., 2004

c Joss et al., 2006

d Jones et al., 2002

e Radjenović et al., 2009

f Carballa et al., 2008

g Maurer et al., 2007

h Hyland, 2014

i Okuda et al., 2009

j Joss et al., 2004

k Stevens-Garmon et al., 2011

l Wick et al., 2009

m Tran et al., 2015

n Blair et al., 2015

CECs have varying biodegradability based on whether the treatment process is aerobic, anoxic, and anaerobic. At the NWRF, both sets of digesters are currently anaerobic. However, the digester modules in GPS-X are not compatible with the MD tool. The digesters have large variability in removal percentages (Table 5-2). However, a lack of modeling could result in incorrect concentrations in the digester effluents.

Table 4-2 and Table 4-3 served as a preliminary list of expected CECs to model. However, some of the CECs listed were below the method reporting limit (MRL) (as noted in the tables). After removal percentages were determined for each CEC (Table 5-2), each pair of indicator and validation CECs was confirmed to have similar removal percentages in the primary clarifiers, PFR, or both unit processes. In contrast to base model calibration, instead of adjusting just model parameters, CEC rate constants and coefficients were adjusted as part of the calibration process.

## Expanded and Advanced Models

After the enhanced model was calibrated and validated, the expanded model was developed. The expanded model utilized the enhanced model but was modified with currently proposed (and ongoing) plant expansion treatment processes. This included adjustments to certain treatment processes, as well as a volume expansion of the aeration basin and final clarifiers. The current plant expansion also includes the addition of a UV disinfection process. With the initial expanded model developed, multiple scenarios were analyzed to determine the NWRF performance on CEC removal efficiency with varying conditions. Next, in the advanced model, additional AT processes were integrated and analyzed. These processes were simulated to determine their effects on CEC removal efficiency.

## Model Limitations

A portion of the expansion at the NWRF is the addition of UV disinfection. Although GPS-X has a disinfection treatment process, UV is not an option. Furthermore, in order to use a treatment process to model CECs, the unit must be compatible with the MD tool. Although the MD tool is compatible with primarily suspended and attached growth processes, other treatment processes are available. Below, the options given for model generation are shown (Figure 4-1). Since UV was not included as an option in GPS-X, it was not included in the expanded or advanced models.

Figure 4-1: GPS-X Model Generation Treatment Processes

# Results and Discussion

## Sampling and Analysis

Sampling was completed on January 27, 2016. In order to monitor the wastewater as it passed through the plant, samples were taken at different times throughout the day based on the units’ hydraulic retention time (HRT). It was assumed that the data would be more representative of each treatment processes’ removal capability if HRT was taken into consideration. Table 5-1 displays each unit’s estimated HRT along with the time of sampling for each. A few items should be addressed regarding the sampling times and locations:

- The first sampling point was the preliminary treatment effluent. It was assumed that there were no changes in CEC concentrations between the plant influent and preliminary treatment effluent. Therefore, the preliminary effluent only had to be sampled at an early enough time to be able to sample the rest of the plant on the same day.

- The primary and secondary digesters have HRTs of multiple days. Because time was of importance, these treatment processes were sampled at 9:30 AM, without taking HRT into consideration.

- The NWRF does not have a sampling location for the PFR effluent. Therefore, the PFR effluent was actually taken towards the bottom of the secondary clarifier. This should not have a significant effect on the CEC concentrations.

Table 5-1: Treatment Process Sampling Times

| Treatment Process | HRT (hours) | Sampling Time |
| --- | --- | --- |
| Preliminary Treatment Effluent | N/A | 6:37 AM |
| Primary Clarifier Effluent | 3 | 9:35 AM |
| PFR Effluent | 6 | 3:40 PM |
| Secondary Clarifier Effluent | 3 | 6:37 PM |
| Primary Digester Effluent | N/A* | 9:30 AM |
| Secondary Digester Effluent | N/A* | 9:30 AM |

* HRT is several days and was not considered during sampling due to time constraints.

Eurofins Eaton Analytical performed the analysis of 98 CECs. However, only 38 (Table 5-2) of these were above the MRL in one or more of the treatment processes (Appendix B: CECs (and MRLs) Analyzed). Furthermore, each indicator CEC is significantly lower than its MTT concentration. Several CECs increase in concentration as they move through the plant (Table 5-2). If more samples could have been collected (during other days and even seasons), it is likely that fewer CECs would have negative removal percentages. However, it is worth noting that there would likely still be CECs with negative removal percentages. This is due to the fact that biodegraded products can convert back to the parent compound during treatment processes (Jelić et al., 2012). For instance, theobromine could have converted back to caffeine. Due to the high percent removal of both compounds, though, this was likely not the case for theobromine. Negative removal percentages can also be attributed to the desorbing of CECs in a unit operation. Previously sorbed CECs can desorb, causing an increase in concentration. Furthermore, instrumental errors can result in small negative removal percentages (Verlicchi et al., 2012).

Table 5-2: NWRF CEC Removal Percentages

|  | Prelim. Treat. Effl. | Prim. Clar. Effl. | PFR Effl. | Sec. Clar. Effl. | Prim. Dig. Effl. | Sec. Dig. Effl. |
| --- | --- | --- | --- | --- | --- | --- |
| Compound (MTT in ng/L) | ng/L | ng/L | ng/L | ng/L | ng/L | ng/L |
| 1,7-Dimethylxanthine | 4200 | 3500 | 14 | 13 | 18 | 18 |
| 4-nonylphenol - semi quantitative | 1200 | <100 | 460 | 510 | 400 | 570 |
| 4-tert-Octylphenol | 950 | 380 | 330 | 350 | 210 | 390 |
| Acesulfame-K | 26000 | 22000 | 1400 | 1400 | 7400 | 7200 |
| Acetaminophen | 26000 | 12000 | <500 | <500 | <500 | <500 |
| Albuterol | 17 | <5 | <5 | <5 | <5 | <5 |
| Amoxicillin | 15000 | 15000 | 16000 | 18000 | 12000 | 11000 |
| Atenolol (4,000) | 990 | 200 | 100 | 90 | 96 | <5 |
| Atrazine | <5 | <5 | <5 | <5 | 63 | 55 |
| Azithromycin | 290 | 270 | 270 | 200 | 140 | 180 |
| Butalbital | 9.4 | 10 | 10 | 11 | <5 | <5 |
| Caffeine | 45000 | 36000 | <500 | <500 | <500 | <500 |
| Carbamazepine | 88 | 110 | 110 | 110 | 140 | 200 |
| Cotinine | 940 | 710 | 48 | 57 | 240 | 770 |
| DEET (200,000) | 290 | 220 | <100 | <100 | 140 | 300 |
| Diltiazem | 42 | 34 | 27 | 24 | <5 | <5 |
| Estrone (E1) | 12 | <5 | <5 | <5 | <5 | <5 |
| Ethylparaben | 200 | <20 | <20 | <20 | <20 | <20 |
| Gemfibrozil (800,000) | 1500 | 1200 | 1500 | 1400 | 1100 | 1800 |
| Iohexol | 61000 | 44000 | 36000 | 37000 | 5500 | 370 |
| Iopromide (750,000) |  | 410 | 16 | 16 | 28 | 31 |
| Lidocaine | 320 | <5 | 290 | 290 | 270 | <5 |
| Lopressor | 1400 | 3000 | 960 | 1200 | 1500 | 1800 |
| Meprobamate (200,000) | 51 | 34 | 44 | 45 | 42 | 29 |
| Methylparaben | 100 | <20 | <20 | <20 | <20 | <20 |
| Metolachlor | 11 | 11 | 6.9 | 10 | 81 | 74 |
| Naproxen | 140 | 170 | 19 | <10 | 32 | <10 |
| Primidone |  | 88 | 100 | 94 | 69 | 52 |
| Propylparaben | 670 | 180 | 10 | <5 | 24 | 77 |
| Salicylic Acid | 750 | 430 | <100 | <100 | <100 | <100 |
| Simazine | 140 | 150 | 170 | 160 | 7.7 | <5 |
| Sucralose (150,000,000) | 23000 | 4900 | 22000 | 19000 | 26000 | 23000 |
| Sulfamethoxazole | 990 | 1100 | 900 | 1000 | 32 | <5 |
| TCPP | 160 | <100 | 180 | 160 | 410 | <100 |
| Theobromine | 8200 | 6800 | <100 | <100 | <100 | <100 |
| Theophylline | 12000 | 9200 | <200 | <200 | <200 | <200 |
| Triclosan (2,100,000) | 11 | <10 | <10 | <10 | <10 | <10 |
| Trimethoprim | 260 | 310 | 380 | 440 | <50 | <50 |

In the next step, CECs were arranged and graphed according to overall plant removal percentage (Figure 5-1 to Figure 5-6). CECs that have removal percentages greater than 90% generally are significantly (95% confidence interval (CI) of 67.2 to 100% for PFR removal percentage) removed in the PFR. CECs that have removal percentages between 50 and 90% are removed more in the primary clarifiers than in the PFR. CECs with percentage removals lower than 50% do not show any general trends. Several of these compounds increase in concentration during the treatment process, which could be due to biodegraded compound converting back to their parent compounds, desorption of previously sorbed compounds, or sampling/instrumental errors.

Figure 5-1: NWRF CEC Concentrations with Removal Percentage Greater than 95%

* Concentrations were below the MRL in the plant effluent.

**Concentrations were below the MRL in the PFR and plant effluents.

***Concentrations were below the MRL in the primary clarifiers, PFR, and plant effluents.

Figure 5-2: NWRF CEC Concentrations with Removal Percentage between 90 and 95%

* Concentrations were below the MRL in the plant effluent.

**Concentrations were below the MRL in the PFR and plant effluents.

***Concentrations were below the MRL in the primary clarifiers, PFR, and plant effluents.

Figure 5-3: NWRF CEC Concentrations with Removal Percentage between 70 and 90%

* Concentrations were below the MRL in the plant effluent.

**Concentrations were below the MRL in the PFR and plant effluents.

***Concentrations were below the MRL in the primary clarifiers, PFR, and plant effluents.

Figure 5-4: NWRF CEC Concentrations with Removal Percentage between 50 and 70%

* Concentrations were below the MRL in the plant effluent.

**Concentrations were below the MRL in the PFR and plant effluents.

***Concentrations were below the MRL in the primary clarifiers, PFR, and plant effluents.

Figure 5-5: NWRF CEC Concentrations with Removal Percentage between 30 and 50%

* Concentrations were below the MRL in the plant effluent.

**Concentrations were below the MRL in the PFR and plant effluents.

***Concentrations were below the MRL in the primary clarifiers, PFR, and plant effluents.

Figure 5-6: NWRF CEC Concentrations with Removal Percentage between 0 and 30%

* Concentrations were below the MRL in the plant effluent.

**Concentrations were below the MRL in the PFR and plant effluents.

***Concentrations were below the MRL in the primary clarifiers, PFR, and plant effluents.

Averages, standard deviations, and 95% CIs were calculated for each range of CECs (Table 5-3). Several removal percentage groups have only one or two CECs in the group. Because of this, some averages, standard deviations, and 95% CIs have large ranges. For CECs with concentrations below the MRL, the MRL concentrations were used in calculating the removal percentage.

Table 5-3: Statistical Analysis of NWRF CEC Removal Percentages

|  |  | Plant |  |  | Primary Clarifiers |  |  | PFR |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Plant Rem. % | No. of CECs | Avg. Rem. % | Std. Dev. | 95% CI | Avg. Rem. % | Std. Dev. | 95% CI | Avg. Rem. % | Std. Dev. | 95% CI |
| 90 to 100 | 12 | 95.9 | 3.6 | 93.9 - 97.9 | 41.4 | 29.7 | 24.6 - 58.2 | 83.9 | 29.6 | 67.2 - 100 |
| 80 to 90 | 2 | 83.3 | 4.7 | 76.8 - 89.8 | 61.3 | 26.4 | 26.4 - 97.9 | 38.4 | 54.3 | - |
| 70 to 80 | 1 | 70.6 | - | - | 70.6 | - | - | 0.0 | - | - |
| 60 to 70 | 2 | 64.3 | 1.7 | 61.9 - 66.7 | 42.1 | 25.4 | 6.9 - 77.3 | 33.9 | 29.3 | 0 - 74.5 |
| 50 to 60 | 2 | 57.9 | 0.6 | 57.1 - 58.7 | 75.0 | 23.6 | 42.3 - 100 | - | - | - |
| 40 to 50 | 1 | 42.9 | - | - | 19.0 | - | - | 20.6 | - | - |
| 30 to 40 | 2 | 35.2 | 5.9 | 27.0 - 43.4 | 17.4 | 14.8 | 0 - 37.9 | 9.1 | 12.9 | - |
| 20 to 30 | 0 | - | - | - | - | - | - | - | - | - |
| 10 to 20 | 3 | 14.5 | 2.8 | 10.6 - 18.4 | - | - | - | - | - | - |
| >0 to 10 | 4 | 8.6 | 1.3 | 7.3 - 9.9 | 31.9 | 45.1 | - | - | - | - |

Note: Negative removal percentages are not included in average, standard deviation, or 95% CI          calculations.

To narrow the scope of the research, indicator and validator CECs (Table 4-2) were isolated from other CECs and plotted in the same manner as above (Figure 5-7 to Figure 5-9). The total plant removal percentages for each CEC are shown in parentheses in the legend. Almost every CEC that is removed greater than 30% in the overall plant shows moderate removal percentage in the primary and secondary clarifiers and CECs with removal percentages greater than 90% are considerably removed in the PFR. This is expected as VSS and Xa levels are about six and twenty times larger in the PFR than in the clarifiers, respectively (Figure 5-17).

Figure 5-7: Indicator and Validator CECs with Removal Percentage Greater than 90%

Figure 5-8: Indicator and Validator CECs with Removal Percentage between 30 and 90%

Figure 5-9: Indicator and Validator CECs with Removal Percentage between 0 and 30%

The removal percentages of each indicator CEC and its validation CEC were compared (Table 5-4). CECs with large negative removal percentages are not listed and were not included in the scope of this research. Furthermore, for CECs that have large negative removal percentages in any of the treatment processes (meprobamate, gemfibrozil, and sucralose); only the unit that had a positive removal percentage was calibrated in the model. As mentioned, these negative removal percentages can be attributed to a lack of multiple data sets or CECs converting back to their parent compounds (Jelić et al., 2012) or desorption of the compound (Verlicchi et al., 2012). Due to the complexity that this phenomenon would add to the model, these CECs were instead calibrated for the treatment process that showed positive removal percentages.

Due to budgetary constraints, CEC sampling was only done on one day (January 27, 2016). Consequently, the enhanced model was calibrated (CEC biodegradation and adsorption constants were adjusted) using the average influent data for the month of January, 2016 (Table 5-5).

Table 5-4: Removal Percentages of Indicator and Validator CECs

|  |  | Removal Percentage |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Prim. Clar. | PFR | Sec. Clar. | Plant | Sec. Dig. |
| Compound | Class | % | % | % | % | % |
| Meprobamate | Anti-Anxiety Indicator | 33.3 | -29.4 | -2.3 | 11.8 | 31.0 |
| Triclosan | Antibacterial Indicator | >9.1 |  |  | >9.1 |  |
| Atenolol | Beta Blocker Indicator | 79.8 | 50.0 | 10.0 | 90.9 | 100.0 |
| E1 | Hormone Validator | >58.3 |  |  | >58.3 |  |
| Gemfibrozil | Lipid Regulator Indicator | 20.0 | -25.0 | 6.7 | 6.7 | -63.6 |
| DEET | Repellant Indicator | 24.1 | >54.5 |  | >65.5 | -114.3 |
| Caffeine | Stimulant Indicator | 20.0 | >98.6 |  | >98.9 |  |
| Theobromine | Caffeine Degradate Validator | 17.1 | >98.5 |  | >98.8 |  |
| Sucralose | Sugar Substitute Indicator | 78.7 | -349.0 | 13.6 | 17.4 | 11.5 |
| Acesulfame-K | Sugar Substitute Validator | 15.4 | 93.6 | 0.0 | 94.6 | 2.7 |
| Iopromide | X-Ray Contrast Agent Indicator |  | 96.1 | 0.0 |  | -10.7 |
| Iohexol | X-Ray Contrast Agent Validator | 27.9 | 18.2 | -2.8 | 39.3 | 93.3 |

Table 5-5: Average Influent Conditions for January 2016

| Influent Parameters |  |
| --- | --- |
| Temperature | 17.1°C |
| Influent Flow (split) | 4.985 MGD |
| pH | 7.44 |
| TSS | 161 mg/L |
| cBOD5 | 263 mg/L |
| Ammonia | 20.7 mg/L |
| DO | 0.6 mg/L |

## Base Model

Preliminary steps of this research included the development, calibration, and validation of the base model. As mentioned, due to the size of the NWRF, the plant had to be divided in half (Table 4-1 and Figure 5-10).

Figure 5-10: GPS-X Base Model Layout

In the GPS-X model, the influent passes through a bar screen and grit chamber before it is split to the two primary clarifiers (60% to the 0.288 million gallon (MG) clarifier and 40% to the 0.200 MG clarifier). The flow then combines into the PFR aeration basin, where it goes through three separate chambers in series. Next, the flow is split again to the secondary clarifiers (34% to the 0.676 MG clarifier and 66% to the 1.33 MG clarifier). The settled material from the primary clarifiers and some of the settled biomass, or waste activated sludge (WAS), from the secondary clarifiers are combined and split again (50%-50%) to the sludge thickeners. The remaining settled biomass, or return activated sludge (RAS), is recycled to the influent of the PFR. The secondary clarifier effluent is combined and released from the WWTP. From the thickeners, the thickened sludge goes through the two anaerobic digesters in series. The residual water from the thickeners and digesters is brought back to the front of the plant upstream of the belt screen.

### Base Model Calibration

After the base model was developed, it was calibrated using daily NWRF cBOD, TSS, and ammonia data for the entire year of 2013. To analyze the accuracy of the model, measured and modeled concentrations of these three constituents, along with the 30-day moving average of the measured data, were plotted together (Figure 5-11 to Figure 5-13). The residual sum of squares (RSS) (Equation 5.1) and explained sum of squares (ESS) (Equation 5.1) were calculated for each constituent over the entire year and are displayed in the figures.

| RSS=i=1n(yi-yi)2 | Equation 5.1 |
| --- | --- |

where

n is the number of number of observations

yi is the measured constituent concentration at day i, and

ŷi is the modeled constituent concentration at day i.

| ESS=i=1n(yi-y)2 | Equation 5.2 |
| --- | --- |

where

ȳ is the mean of the measured constituent concentration.

Figure 5-11: 2013 Measured and Modeled Effluent cBOD (RSS=1145.9 and ESS=153.5)

Figure 5-12: 2013 Measured and Modeled Effluent TSS (RSS=1724.4 and ESS=613.8)

Figure 5-13: 2013 Measured and Modeled Effluent Ammonia (RSS=40.3 and ESS=29.7)

Modeled TSS is higher than measured TSS in the warmer months (Figure 5-12). Conversely, in 2012 data (the validator year), modeled TSS is lower than measured TSS in these months.  However, adjusting settling characteristics to account for this resulted in either the calibrated year or validated year showing accurate results, but not both. The same can be said for adjusting Arrhenius coefficients for cBOD and ammonia.

During calibration, because of a lack of data, several RAS and secondary clarifier WAS rates were analyzed. As expected, both parameters proved to have a significant influence on cBOD and TSS concentrations. After analyzing various RAS and WAS flows and slightly adjusting other model parameters (influent BOD and nutrient ratios, PFR ratios and stoichiometry, and settling characteristics), a RAS of 70% and secondary clarifier WAS of 4% of the total influent flow were found to result in the lowest combined RSS (cBOD=1145.9; TSS=1724.4; and ammonia=40.3) for all three constituents in the calibration year.

### Base Model Validation

After adjustments were made for the base model calibration, the same parameters were used for base model validation. Although measured data from the validation year (2012) varied significantly, the modeled data generally provided reasonable results (RSS values: cBOD=1747.7; TSS=961.4; and ammonia=69.4) (Figure 5-14 to Figure 5-16). As mentioned, adjusting settling characteristics could result in the calibration year or validation year being more accurate, but not both. The settling characteristics used herein resulted in the lowest RSS for TSS between both calibration and validation years. Similarly, adjusting Arrhenius coefficients proved that the model could be calibrated to reduce RSS values for the calibration or validation year, but not both. Additionally, as cBOD is a function of RAS and secondary clarifier WAS rates, both could be adjusted to result in cBOD modeled data that lowered RSS. In fact, calibration revealed that RAS and secondary clarifier WAS had the largest effect on effluent results. However, with no data to support changing these rates, 70% (RAS) and 4% (secondary clarifier WAS) were assumed. This research, as shown in Sections 5.4.1 and 5.4.4, analyzed plant efficiency under various RAS and WAS rates.

Figure 5-14: 2012 Measured and Modeled Effluent cBOD (RSS=1747.7 and ESS =500.1)

Figure 5-15: 2012 Measured and Modeled Effluent TSS (RSS=961.4 and ESS =317.7)

Figure 5-16: 2012 Measured and Modeled Effluent Ammonia (RSS=69.4 and ESS=40.4)

## Enhanced Model

After base model calibration and validation, the MD tool was used to incorporate CECs and biodegradation and adsorption reactions and constants into the model. Because it allows for customizable state variables, the Carbon, Nitrogen, Phosphorus, Custom Components library (cnpiplib) was used. By coding some of the text files associated with this library, CEC names were entered into the model. GPS-X separates customizable state variables into soluble and particulate matter (Table 5-6).

Table 5-6: Customizable State Variables and Corresponding CECs

| State Variable Name (Soluble) | Corresponding CEC (Soluble) | State Variable Name (Particulate) | Corresponding CEC (Particulate) |
| --- | --- | --- | --- |
| sza | Soluble E1 | xza | Particulate E1 |
| szb | Soluble atenolol | xzb | Particulate atenolol |
| szd | Soluble meprobamate | xzd | Particulate meprobamate |
| sze | Soluble triclosan | xze | Particulate triclosan |
| szf | Soluble gemfibrozil | xzf | Particulate gemfibrozil |
| szg | Soluble DEET | xzg | Particulate DEET |
| szh | Soluble caffeine | xzh | Particulate caffeine |
| szi | Soluble theobromine | xzi | Particulate theobromine |
| szj | Soluble sucralose | xzj | Particulate sucralose |
| szk | Soluble acesulfame-K | xzk | Particulate acesulfame-K |
| szl | Soluble iopromide | xzl | Particulate iopromide |
| szm | Soluble iohexol | xzm | Particulate iohexol |

Most pharmaceuticals have solubility concentrations on the order of mg/L, while concentrations in wastewater are on the order of ng/L (Shraim et al., 2012). Therefore, plant influent CEC concentrations (before adsorption takes place) are assumed to be in the soluble form. During adsorption, the CECs move from soluble to particulate matter and, as shown in Section 5.6, are considerably removed during final sedimentation. Unless specifically noted as “particulate”, all references to CECs in this research are meant as soluble CECs.

The next step in the model developer tool was to set up and populate the Stoichiometry Matrix (Appendix C: Stoichiometry Matrix). Then, Equation 2.2, Equation 2.3, and Equation 2.6 were modified to be entered into the Kinetic Equations section (Appendix D: Kinetic Equations and Equation 5.3 to Equation 5.5). For this case, the equations below are shown for E1 (sza). The three equations were used for every indicator and validator CEC. It should be noted that only state variables can be used in the Kinetic Equations second. In GPS-X, VSS is a composite variable. Therefore, Equation 5.3 had to be modified to include only state variables.

| X=kdE1×sza×VSS =kdE1×sza×(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)icv | Equation 5.3 |
| --- | --- |

where

X is the sorbed CEC concentration (g/m3)

kdE1 is the E1 partitioning coefficient (m3/g)

sza is the soluble E1 concentration (g/m3)

VSS is the volatile suspended solids concentration (g/m3)

icv is the particulate COD to VSS ratio

xs is the slowly biodegradable substrate concentration (g/m3)

xbh is the active heterotrophic biomass concentration (g/m3)

xba is the active autotrophic biomass concentration (g/m3)

xsto is the internal cell storage product concentration (g/m3)

xbp is the active poly-phosphorus accumulating biomass concentration (g/m3)

xbt is the polyhydroxyalkanoates concentration (g/m3)

xgly is the stored glycogen concentration (g/m3)

xi is the particulate inert organic material concentration (g/m3), and

xu is the unbiodegradable particulates from cell decay concentration (g/m3)

| rdes=kdes×xza | Equation 5.4 |
| --- | --- |

where

rdes is the rate of adsorption of particulate E1 (m3/g · d)

kdes is the desorption coefficient (1/d), and

xza is the particulate E1 concentration (g/m3)

| rbio=-kbioE1×sza×xbh | Equation 5.5 |
| --- | --- |

where

rbio is the rate of biodegradation of the CEC (g/m3 · d)

kbioE1 is the E1 biodegradation constant (g/m3 · d)

sza is the soluble E1 concentration (g/m3), and

xbh is the active heterotrophic biomass concentration (g/m3)

Next, because the biodegradation and sorption constants are not defined in the model, they were added using the Kinetic Parameters section (Appendix E: Kinetic Parameters). Here, sorption and biodegradation constants were defined and assigned values within the model.

During the enhanced model development, it was discovered that the PFR was able to handle the modified model fairly easily. However, when the same model was developed for the primary clarifiers, the model slowed significantly. For the secondary clarifiers, the model became nonresponsive. Due to the low removal percentages in the secondary clarifiers, (no indicator or validator CEC was removed more than 13.6% (Table 5-4)) they were not modeled in this research.

### Enhanced Model Calibration and Validation

During enhanced model calibration, biodegradation was found to have a larger effect on CEC removal than adsorption. This is evidenced by the general trend of CEC biodegradation constants being larger than their partitioning constants (Table 4-2 and Table 4-3). Although VSS is greater than the active heterotrophic biomass (Xa) concentration (Figure 5-17) in each treatment process, it is not a large enough difference to offset the differences in biodegradation and adsorption constants.

Figure 5-17: Modeled VSS and Xa Concentrations during Sampling

To calibrate the enhanced model, the biodegradation and adsorption constants were varied until modeled CEC concentrations matched measured concentrations. When possible, the constants were kept as close to literature values as possible. However, in some cases, this was not possible, as literature values resulted in effluent concentrations higher or lower than measured data (Table 5-7).

Table 5-7: Calibrated Biodegradation and Adsorption Constants

|  | kbio (L/g-d) |  | Kd (L/kg) |  |
| --- | --- | --- | --- | --- |
|  | Literature | Modeled | Literature | Modeled |
| Meprobamate | - | 0 | 316.2-631.0 | 790.0 (Prim. Clar.) |
| Triclosan | 1.2-3.6 | 1.2 | 1905-9550 | 1905.0 |
| Atenolol | 0.69-2.2 | 4.2 | 0.21-152 | 300.0 |
| E1 | 162±25 | 162.0 | 170-362 | 170.0 |
| Gemfibrozil | 6.4-9.6 | 0.0 (Prim. Clar.) | 10.0-1106 | 400.0 (Prim. Clar.) |
| DEET | - | 1.5 | 58.9-1258.9 | 100.0 |
| Caffeine | 39.6-50.9 | 0.4 (Prim. Clar.) 40.0 (PFR)┼ | 199.5-794.3 | 200.0 |
| Theobromine | ^ | 0.38 (Prim. Clar.) 38.0 (PFR) ┼ | ^ | 200.0 |
| Sucralose | 0.003-0.009 | .0065 (Prim. Clar.) | 66.6-1084.6 | 540.0 (Prim. Clar.) |
| Acesulfame-K | 0.0448-0.0594 | 0.0613 (Prim. Clar.) 10.0 (PFR) ┼ | 42.5-704.3 | 170.0 |
| Iopromide | 1.6-2.5 | 7.5┼ | 6.9-12 | 36.0┼ |
| Iohexol | 1.8-2.4 | 0.8 | - | 0 |

┼ The calibrated constant was determined using removal efficiency rather than concentration.

As noted, PFR biodegradation constants for caffeine, theobromine, acesulfame-K, and iopromide were determined using PFR removal percentages rather than the actual concentration. Caffeine, theobromine, and acesulfame-K were removed more in the PFR than in the primary clarifiers while the influent data for iopromide was reported to be below MRL. Without developing an entirely new model for treatment processes with different biodegradation constants, there was no way to use different values for the primary clarifiers and PFR. Therefore, for caffeine, theobromine, and acesulfame-K, the model was first analyzed using primary clarifier constants. Then, kbio was adjusted in a separate analysis until the modeled removal percentages closely matched the measured removal percentages. For iopromide, only one analysis was used to match the modeled PFR removal percentage with the measured PFR removal percentage.

Due to negative removal percentages in the PFR, biodegradation and adsorption constants for meprobamate, gemfibrozil, and sucralose were only determined for the primary clarifiers. Throughout the remainder of the analyses, these three compounds are only analyzed in the primary clarifier.

Both E1 and triclosan had PFR, secondary clarifier, and effluent concentrations below the MRL. Therefore, the minimum literature biodegradation and adsorption constants that resulted in modeled effluent concentrations below the MRL were used.

The only calibration and validation CECs that perform the same throughout the NWRF are caffeine and theobromine. Because theobromine is a product of caffeine degradation (Asano et al., 1993), this is expected. Although sucralose and acesulfame-K are removed similarly in the primary clarifiers, acesulfame-K is more highly biodegraded in the PFR than sucralose. The partitioning coefficients for iohexol and iopromide are both well above each CEC’s literature value. Iohexol, though, has a higher biodegradation constant than iopromide. From the constants in Table 5-7, concentrations of each CEC were plotted for each treatment process (Figure 5-18 to Figure 5-29).

Figure 5-18: Enhanced Model Meprobamate Concentrations under Sampling Conditions

Figure 5-19: Enhanced Model Triclosan Concentrations under Sampling Conditions

Figure 5-20: Enhanced Model Atenolol Concentrations under Sampling Conditions

Figure 5-21: Enhanced Model E1 Concentrations under Sampling Conditions

Figure 5-22: Enhanced Model Gemfibrozil Concentrations under Sampling Conditions

Figure 5-23: Enhanced Model DEET Concentrations under Sampling Conditions

Figure 5-24: Enhanced Model Caffeine Concentrations under Sampling Conditions

Figure 5-25: Enhanced Model Theobromine Concentrations under Sampling Conditions

Figure 5-26: Enhanced Model Sucralose Concentrations under Sampling Conditions

Figure 5-27: Enhanced Model Acesulfame-K Concentrations under Sampling Conditions

Figure 5-28: Enhanced Model Iopromide Concentrations under Sampling Conditions

Figure 5-29: Enhanced Model Iohexol Concentrations under Sampling Conditions

Most CECs are removed predominantly by biodegradation. Generally, CECs are removed more in the PFR than in the primary clarifiers. Furthermore, CECs with higher removal percentages are more affected by biodegradation than by adsorption. While biodegradation and adsorption averages are similar in the primary clarifier, biodegradation becomes the dominant removal mechanism in the PFR (Table 5-8). The percent removed by biodegradation is calculated by dividing the concentration removed of a given CEC due to biodegradation by the total amount the CEC is removed (from biodegradation and adsorption) in each treatment process. The percent adsorption is the concentration removed due to adsorption divided by the total concentration removed.

Table 5-8: Enhanced Model Biodegradation vs. Adsorption during Sampling

| CEC | Treatment Process | Percent of Total Removal |  |  |
| --- | --- | --- | --- | --- |
|  |  | Biodegradation | Adsorption | Total |
| Meprobamate* | Primary Clarifier | 0.0% | 100.0% | 100.0% |
|  | PFR | 0.0% | 100.0% | 100.0% |
| Triclosan | Primary Clarifier | 34.4% | 65.6% | 100.0% |
|  | PFR | 69.5% | 30.5% | 100.0% |
| Atenolol | Primary Clarifier | 90.3% | 9.7% | 100.0% |
|  | PFR | 98.9% | 1.1% | 100.0% |
| E1 | Primary Clarifier | 100.0% | 0.0% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Gemfibrozil* | Primary Clarifier | 0.4% | 99.6% | 100.0% |
|  | PFR | 0.3% | 99.7% | 100.0% |
| DEET | Primary Clarifier | 87.8% | 12.2% | 100.0% |
|  | PFR | 96.2% | 3.8% | 100.0% |
| Caffeine | Primary Clarifier | 51.3% | 48.7% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Theobromine | Primary Clarifier | 49.9% | 50.1% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Sucralose* | Primary Clarifier | 0.9% | 99.1% | 100.0% |
|  | PFR | 1.9% | 98.1% | 100.0% |
| Acesulfame-K | Primary Clarifier | 16.1% | 83.9% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Iopromide | Primary Clarifier | - | - | - |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Iohexol | Primary Clarifier | 100.0% | 0.0% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Average | Primary Clarifier | 48.3% | 51.7% | 100.0% |
|  | PFR | 72.2% | 27.8% | 100.0% |

## * Modeled concentrations were used because measured concentrations showed negative removal percentages.

## Expanded Model

After calibration of the enhanced model, the NWRF expansion was incorporated into the model, creating the expanded model. The only changes in the model from the current NWRF layout (Table 4-1) are the addition of an identical PFR (0.495 MG per chamber) and a secondary clarifier (1.33 MG). Because the PFR volume will increase by 100% and the final clarifier by 66%, an adjusted flowrate that is 75% greater than the most recent flowrate data is used. In keeping the other parameters constant (Table 5-5), CEC removal percentages for the expanded and enhanced model were compared (Figure 5-30 to Figure 5-41).

As mentioned, as part of the plant expansion, the NWRF will also incorporate UV disinfection as one of the last treatment processes. Unfortunately, GPS-X is unable to model UV disinfection. Like other oxidants, UV removal is largely dependent on concentration-time (or intensity-time in the case of UV) (Lee et al., 2009). In two studies, CEC removal percentage ranged from 1 to 90%, depending on the intensity-time provided by the UV lamps and the pH (Canonica et al., 2008; Kim et al., 2009).

Figure 5-30: Expanded Model Meprobamate Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-31: Expanded Model Meprobamate Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-32: Expanded Model Atenolol Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-33: Expanded Model E1 Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-34: Expanded Model Gemfibrozil Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-35: Expanded Model DEET Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-36: Expanded Model Caffeine Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-37: Expanded Model Theobromine Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-38: Expanded Model Sucralose Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-39: Expanded Model Acesulfame-K Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-40: Expanded Model Iopromide Concentrations under Sampling Conditions (Modified Flowrate)

Figure 5-41: Expanded Model Iohexol Concentrations under Sampling Conditions (Modified Flowrate)

The expanded model has higher CEC concentrations in the primary clarifier effluent (Figure 5-30 to Figure 5-41). Because the expanded plant does not include an additional primary clarifier, it is likely that CEC concentrations are higher due to the increased flow rate per clarifier. In some cases, the additional PFR is able to compensate for the lack of an additional primary clarifier. Triclosan, atenolol, E1, DEET, caffeine, theobromine, iopromide, and iohexol all show similar, if not lower, concentrations in the expanded PFRs when compared to the enhanced PFR. When using 70% RAS for both the enhanced and expanded models, the primary clarifiers in both have similar VSS and Xa concentrations (Figure 5-42). In the PFR, expanded model VSS and Xa concentrations are noticeably larger. This implies that the rate of biodegradation and the amount of sorbed compound are larger in the expanded model PFRs, confirming the conclusions drawn from Figure 5-30 to Figure 5-41.

Figure 5-42: Expanded vs. Enhanced Model VSS and Xa Concentrations

Biodegradation and adsorption were compared in the primary clarifiers and the PFRs for the expanded model (Table 5-9). As with the enhanced model (Table 5-8), removal due to biodegradation and adsorption is roughly equal in the primary clarifier. Biodegradation in the PFRs becomes slightly higher in the expanded model because of the additional PFR. Because biodegradation is the primary removal mechanism (Table 5-8) in the PFRs, this is expected. VSS is over three times larger than Xa in the primary clarifiers (Figure 5-42). However, because biodegradation rates are typically larger than adsorption rates (Table 5-7), removal from biodegradation and adsorption are almost equal in the primary clarifiers. In the PFRs, VSS and Xa concentrations are closer together. This allows biodegradation to become the primary removal mechanism.

Table 5-9: Expanded Model Biodegradation vs. Adsorption in the Expanded Model

| CEC | Treatment Process | Percent of Total Removal |  |  |
| --- | --- | --- | --- | --- |
|  |  | Biodegradation | Adsorption | Total |
| Meprobamate* | Primary Clarifier | 0.1% | 99.9% | 100.0% |
|  | PFR | 0.1% | 99.9% | 100.0% |
| Triclosan | Primary Clarifier | 33.2% | 66.8% | 100.0% |
|  | PFR | 76.7% | 23.3% | 100.0% |
| Atenolol | Primary Clarifier | 90.4% | 9.6% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| E1 | Primary Clarifier | 100.0% | 0.0% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Gemfibrozil* | Primary Clarifier | 0.0% | 100.0% | 100.0% |
|  | PFR | 0.0% | 100.0% | 100.0% |
| DEET | Primary Clarifier | 90.5% | 9.5% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Caffeine | Primary Clarifier | 56.1% | 43.9% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Theobromine | Primary Clarifier | 54.9% | 45.1% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Sucralose* | Primary Clarifier | 1.2% | 98.8% | 100.0% |
|  | PFR | 2.4% | 97.6% | 100.0% |
| Acesulfame-K | Primary Clarifier | 19.8% | 80.2% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Iopromide | Primary Clarifier | - | - | - |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Iohexol | Primary Clarifier | 100.0% | 0.0% | 100.0% |
|  | PFR | 100.0% | 0.0% | 100.0% |
| Average | Primary Clarifier | 49.7% | 50.3% | 100.0% |
|  | PFR | 73.3% | 26.7% | 100.0% |

## * Modeled concentrations were used because measured concentrations showed negative removal percentages.

After comparing the enhanced and expanded model with parameters from the day of sampling, the expanded model was then extrapolated and examined over an entire year (Figure 5-43 to Figure 5-54). With the exception of flow (which is 75% higher in the expanded model), influent data from 2013 is used in the analysis of the daily expanded model. With the exception of meprobamate, gemfibrozil, and sucralose, the model output predicts the expected CEC concentration when the NWRF is expanded.

Figure 5-43: Expanded Extrapolated Meprobamate Concentrations

* Due to negative removal percentage in the PFR, the CEC was only calibrated in the primary clarifiers.

Figure 5-44: Expanded Extrapolated Triclosan Concentrations

* Measured effluent concentration was below the MRL.

Figure 5-45: Expanded Extrapolated Atenolol Concentrations

Figure 5-46: Expanded Extrapolated E1 Concentrations

* Measured effluent concentration was below the MRL.

Figure 5-47: Expanded Extrapolated Gemfibrozil Concentrations

* Due to negative removal percentage in the PFR, the CEC was only calibrated in the primary clarifiers.

Figure 5-48: Expanded Extrapolated DEET Concentrations

* Measured effluent concentration was below the MRL.

Figure 5-49: Expanded Extrapolated Caffeine Concentrations

* Measured effluent concentration was below the MRL.

Figure 5-50: Expanded Extrapolated Theobromine Concentrations

* Measured effluent concentration was below the MRL.

Figure 5-51: Expanded Extrapolated Sucralose Concentrations

* Due to negative removal percentage in the PFR, the CEC was only calibrated in the primary clarifiers.

Figure 5-52: Expanded Extrapolated Acesulfame-K Concentrations

Figure 5-53: Expanded Extrapolated Iopromide Concentrations

Figure 5-54: Expanded Extrapolated Iohexol Concentrations

Modeled CECs have similar removal patterns throughout the entire year of modeling. Most CECs reach their maximum concentration sometime in the middle of the year and decrease around 230 days. It should be noted that this assumes the same influent concentration of each CEC throughout the entire year. Because calibrated biodegradation and adsorption constants were only found in the primary clarifier for meprobamate, gemfibrozil, and sucralose, these CECs have higher removals in the expanded model than in the measured data (each CEC had negative plant removal percentages). Although they have varying removal percentages, each CEC decreases in concentration around a time of 230 days. This is likely due to increasing VSS and Xa concentrations at this time (Figure 5-55 to Figure 5-56), as well as an increase in water temperature (Figure 5-57).

Figure 5-55: Expanded Model Primary Clarifier and PFR VSS Concentrations

Figure 5-56: Expanded Model Primary Clarifier and PFR Xa Concentrations

Figure 5-57: Daily Water Temperature

### RAS Analysis

After analyzing the expanded plant with the estimated RAS from base model calibration (70%), VSS, Xa, and the CECs were analyzed with varying RAS rates. In this case, RAS is equal to the total recycle flow divided by the total influent flowrate and comes from the settled solids in the secondary clarifiers. Because RAS does not require physical alteration of the plant, it is a reasonable change that can be made to the plant. While primary clarifier VSS and Xa decrease with increasing RAS, PFR concentrations increase (Figure 5-58 to Figure 5-59). Because RAS is pumped from the settled solids area in the secondary clarifiers to the influent of the PFR, concentrations in the PFR increase as the RAS flow increases. Both VSS and Xa have a greater rate of change at lower RAS rates. In the primary clarifier, both decrease at approximately equal rates of change. In the PFRs, VSS increases at a greater rate than Xa as RAS increases. As RAS approaches 100%, it has less effect on concentration. As RAS increases, plant effluent VSS increases and Xa decreases (Figure 5-60).

Figure 5-58: Primary Clarifier VSS and Xa with Varying RAS

Figure 5-59: PFR VSS and Xa with Varying RAS

Figure 5-60: Plant Effluent VSS and Xa with Varying RAS

The decrease in VSS and Xa in the primary clarifiers results in a higher concentration of CECs as RAS increases (Figure 5-61 to Figure 5-63). Because VSS and Xa increase in the PFRs, most CECs have increased removal percentages (Figure 5-64 to Figure 5-66). Due to the small differences in removal percentage, the CECs have been grouped in ranges.

Figure 5-61: Primary Clarifier CEC Removal with Varying RAS (0-30% Removal)

Figure 5-62: Primary Clarifier CEC Removal with Varying RAS (35-65% Removal)

Figure 5-63: Primary Clarifier CEC Removal with Varying RAS (70-100% Removal)

Each CEC has a lower removal percentage in the primary clarifiers as RAS increases (Figure 5-61 to Figure 5-63). Acesulfame-K, gemfibrozil, caffeine, theobromine, iohexol, sucralose, and meprobamate do not have significant removal changes after about 50% RAS. DEET, atenolol, triclosan, and iopromide have a greater rate of decreasing removal at low RAS but start to level off as RAS approaches 100%.

Figure 5-64: PFR CEC Removal with Varying RAS (20-40% Removal)

Figure 5-65: PFR CEC Removal with Varying RAS (40-60% Removal)

Figure 5-66: PFR CEC Removal with Varying RAS (80-100% Removal)

In the PFRs, iohexol has the greatest increase in removal percentage (~8%) of any CEC modeled (Figure 5-64). Triclosan, atenolol, iopromide, acesulfame-K, E1, caffeine, and theobromine do not show any considerable removal change above a RAS of about 30%. However, some of these CECs (triclosan, atenolol, iopromide, and acesulfame-K), display gradually smaller removal percentages as RAS approaches 100%.

Ultimately, due to the decreased removal percentage in the primary clarifiers and the increased removal percentages in the PFR, RAS proved to have a small effect on the total plant CEC removal. CECs that are equally removed in the primary clarifiers and the PFRs (atenolol and triclosan) tend to decrease in removal percentage as RAS increases. CECs with reliance on the PFR for removal (iohexol, DEET, and acesulfame-K) behave the opposite, as RAS increased, the CEC’s removal percent also increased (Figure 5-67 to Figure 5-68).

Figure 5-67: Plant CEC Removal with Varying RAS (10-50% Removal)

Figure 5-68: Plant CEC Removal with Varying RAS (60-100% Removal)

To further analyze RAS effects, other plant effluent parameters were compared. Variability in RAS has a larger effect on TSS than it does cBOD or TKN (Figure 5-69). While cBOD and ammonia stay relatively constant with increasing RAS, TSS increases. Similar to VSS, TSS in the RAS stream causes an increase in concentration in both the PFR and the plant effluent.

Figure 5-69: Plant Effluent TSS, cBOD, and TKN with Varying RAS

### Primary Clarifier Volume Analysis

Next, primary clarifier volume’s effect on CEC removal was examined. The analysis was completed for primary clarifier volume ranging from 57% to 200% of the size of the current primary clarifiers. In general, primary clarifier has a larger effect on CEC removal than RAS. First, the removal percentages of the primary clarifiers were analyzed. Although primary clarifier, PFR, and plant effluent VSS and Xa decrease with increasing primary clarifier volume (Figure 5-70 to Figure 5-72), CEC removal percentage in the primary clarifier increase due to the increased HRT (Figure 5-73). With increased HRT, CECs have longer time to biodegrade.

Figure 5-70: Primary Clarifier VSS and Xa with Varying Primary Clarifier Volume

Figure 5-71: PFR VSS and Xa with Varying Primary Clarifier Volume

Figure 5-72: Effluent VSS and Xa with Varying Primary Clarifier Volume

Figure 5-73: Primary Clarifier CEC Removal with Varying Primary Clarifier Volume

Each modeled CEC decreases in primary clarifier effluent concentration as primary clarifier volume increases (Figure 5-73). As expected, CECs that are more removed in the primary clarifiers (sucralose, triclosan, and iopromide) were more influenced by primary clarifier volume. However, even CECs that are initially removed primarily by the PFR (Figure 5-7) experience at least some increase in removal percentage as volume increases. Next, the PFR was analyzed under varying primary clarifier volumes (Figure 5-74 to Figure 5-75).

.

Figure 5-74: PFR CEC Removal with Varying Primary Clarifier Volume (33-67% Removal)

Figure 5-75: PFR CEC Removal with Varying Primary Clarifier Volume (67-100% Removal)

As primary clarifier volume increases, the removal percentages of iohexol, DEET, atenolol, iopromide, acesulfame-K, theobromine, and caffeine slightly decrease. Meanwhile, triclosan and DEET’s removal percentages both decrease by about 10%. In general, as the volume of the primary clarifier increases, the percent removal observed in the PFR decreases. This can be attributed to two reasons. First, there are lower concentrations of VSS and Xa in the PFR, as they are being more removed in the primary clarifiers (Figure 5-71). Second, because the primary clarifiers are also removing higher percentages of CECs, there is a lower concentration entering the PFR (Figure 5-73). Biodegradation and adsorption are first-order with respect to CEC concentration and Xa and VSS concentrations, respectively. Because of this relationship, removal rates decrease. Although the PFR removal decreases, because of the increased primary clarifier removal, the overall plant removal for most CECs increases with increased primary clarifier volume (Figure 5-76 to Figure 5-77).

Figure 5-76: Plant CEC Removal with Varying Primary Clarifier Volume (33-67% Removal)

Figure 5-77: Plant CEC Removal with Varying Primary Clarifier Volume (67-100% Removal)

Although the difference is small, as the primary clarifier volume increases, CEC removal increases. Interestingly, though, the removal percentage for each CEC increases at approximately the same rate. This indicates that, while biodegradation and adsorption constants are important factors in determining the removal percentage of each CEC, primary clarifier HRT helps to improve removal, regardless of the biodegradation and adsorption rates. However, as primary clarifier volume is doubled, most CEC removal percentages increase only by 3 to 4%.

### Primary Clarifier WAS Analysis

The next operational modification analyzed was the primary clarifier waste activated sludge (WAS) (defined as waste flowrate divided by plant flowrate) rates. During calibration, a primary clarifier WAS of 0.095% was used (0.0083 MGD). Analysis indicated that primary clarifier WAS has minimal effect on VSS, Xa, and thus, on CEC removal (Figure 5-78 to Figure 5-80).

Figure 5-78: Primary Clarifier VSS and Xa with Varying Primary Clarifier WAS

Figure 5-79: PFR VSS and Xa with Varying Primary Clarifier WAS

Figure 5-80: Effluent VSS and Xa with Varying Primary Clarifier WAS

Due to the small decrease of VSS and Xa in the primary clarifiers and PFRs, CEC removal percentages slightly decrease with increased WAS. Due to the small removal percentage decrease in the primary clarifiers and PFRs, only the effluent removal change is shown (Figure 5-81 to Figure 5-82). Each CEC modeled experiences a slight decrease in removal percentage as primary clarifier WAS increases.

Figure 5-81: Plant CEC Removal with Varying Primary Clarifier WAS (40-65% Removal)

Figure 5-82: Plant CEC Removal with Varying Primary Clarifier WAS (75-100% Removal)

### Secondary Clarifier WAS Analysis

The next variable analyzed was the secondary clarifier WAS. Because the SRT in the PFR is a function of the wastage flowrate (Figure 5-83), secondary clarifier WAS has a large effect on CEC concentrations.

Figure 5-83: SRT vs. Secondary Clarifier WAS

The SRT in the current NWRF layout (base model) is about 8 days. In the expanded model, this SRT is achieved with a WAS of approximately 2% of the influent flow. In the primary clarifier, as secondary clarifier WAS increases, VSS and Xa increase (Figure 5-84). However, the rate of increase is smaller after a WAS of about 4.5%. Interestingly, PFR VSS and Xa increase until WAS reaches this 4.5%. After this point, VSS and Xa begin to decrease with increased WAS (Figure 5-85). This indicates a critical point for WAS, and thus SRT. As will be shown, a secondary clarifier WAS in this range allows for optimal removal of CECs (Figure 5-91 to Figure 5-93). Furthermore, plant effluent VSS and Xa levels off at a WAS of about 4.5% (Figure 5-86). Past this point, effluent concentrations do not decrease significantly.

Figure 5-84: Primary Clarifier VSS and Xa with Varying Secondary Clarifier WAS

Figure 5-85: PFR VSS and Xa with Varying Secondary Clarifier WAS

Figure 5-86: Effluent VSS and Xa with Varying Secondary Clarifier WAS

Due to the increased VSS and Xa, secondary clarifier WAS is influential on CEC removal in the primary clarifiers. Almost every CEC experiences increased removal as WAS increases (Figure 5-87).

Figure 5-87: Primary Clarifier CEC Removal with Varying Secondary Clarifier WAS

Each CEC modeled (with the exception of iopromide) experiences increased primary clarifier removal percentage as secondary clarifier WAS increases. As WAS approaches 0%, several CECs approach 0% removal. However, some CECs experience an increase of about 10-15% in removal percentage as WAS approaches 8%. While primary clarifier removal is increased, PFR removal decreases with increased WAS (Figure 5-88 to Figure 5-90). After WAS reaches about 4.5%, VSS and Xa decrease, resulting in decreased CEC removal percentages in the PFR (Figure 5-85).

Figure 5-88: PFR CEC Removal with Varying Secondary Clarifier WAS (30-50% Removal)

Figure 5-89: PFR CEC Removal with Varying Secondary Clarifier WAS (50-70% Removal)

Figure 5-90: PFR CEC Removal with Varying Secondary Clarifier WAS (80-100% Removal)

For each CEC modeled, PFR CEC removal is relatively unchanged until WAS reaches 3.5 to 4%. At this point, removal percentages for iohexol, DEET, and atenolol decrease by 5% or more. Triclosan and acesulfame-K decrease in removal percentage by about 2%. For this reason, 4.5% is considered a critical point for WAS, which corresponds to a SRT of 4.2 days. It is this range that plant CEC removal is optimum (Figure 5-91 to Figure 5-93).

Figure 5-91: Plant CEC Removal with Varying Secondary Clarifier WAS (30-70% Removal)

Figure 5-92: Plant CEC Removal with Varying Secondary Clarifier WAS (55-75% Removal)

Figure 5-93: Plant CEC Removal with Varying Secondary Clarifier WAS (80-100% Removal)

The critical secondary clarifier WAS range for CEC removal is between 2 and 5% (Figure 5-91 to Figure 5-93). This critical WAS can also be seen when analyzing TSS, cBOD, and TKN (Figure 5-94). As shown, all three of these parameters reach a near-minimum point in this range. In this range, most CECs experience maximum removal. Secondary clarifier WAS proved to be the operational change that had the largest effect on CEC removal. Iohexol and DEET experience up to 5% change in removal percentage as WAS varies. Compared with RAS and primary clarifier volume, this is a significant effect. Because WAS is an operational parameter, adjusting WAS to control CEC concentrations is a feasible consideration.

Figure 5-94: Plant Effluent TSS, cBOD, and TKN with Varying Secondary Clarifier WAS

## Advanced Model

After the analysis of several parameters in the expanded model, the advanced model was developed by replacing the PFRs with membrane bioreactors (MBRs). The MBRs are modeled using the same volume as the PFRs, and each has three chambers. Unlike the PFRs in GPS-X, MBRs use internal recycle as their RAS. Rather than have a line from the settled matter in the secondary clarifier like with the PFR, the MBR recycles from the third chamber to the first. Furthermore, with the PFRs, WAS flow from the secondary clarifiers controls the SRT in the reactors. With the MBR, pumped flow from the MBR (WAS) itself controls the SRT (Figure 5-95).

Figure 5-95: PFR vs. MBR Effluent, RAS, and WAS in GPS-X

Because the NWRF does not currently have MBRs, the first step in modeling was to evaluate the sensitivity of CEC removals to changes in RAS and WAS. WAS from the secondary clarifier was also examined but had minimal effect on CEC removal. This is due to the fact that the secondary clarifier only receives filtrate water. Therefore, even the settled solid concentrations in the secondary clarifier are low. After the analysis of RAS and WAS, the optimized advanced plant could be analyzed and compared to the enhanced plant.

### MBR WAS Analysis

As mentioned, WAS is one of the controlling factors in SRT. In the MBR, WAS is defined as the waste flowrate per MBR divided by the influent flowrate to each MBR. As WAS increases, SRT decreases (Figure 5-96).

Figure 5-96: SRT vs. MBR WAS

In the primary clarifier, as WAS increases, Xa also increases. VSS reaches a maximum point at a WAS of 2%. After this point, it decreases until WAS reaches approximately 6%. As WAS approaches 10%, VSS slightly increases (Figure 5-97).

Figure 5-97: Primary Clarifier VSS and Xa with Varying MBR WAS

MBR WAS follows a similar VSS and Xa concentration pattern to secondary clarifier WAS with a PFR (Figure 5-84). In the MBRs, both RAS and WAS streams have equal concentrations. Furthermore, these streams are equal to the concentrations found in the third chamber of the MBR. During WAS variation, all three chambers follow the same VSS and Xa trends, so chambers one and two are not shown.

Figure 5-98: MBR RAS and WAS Streams VSS and Xa with Varying MBR WAS

While Xa decrease is gradual, VSS decreases exponentially with increased WAS. The dramatic decrease in VSS is likely the cause of the maximum point found in the primary clarifiers. At low WAS, because the VSS is largely removed by the membrane (Figure 5-99), higher concentrations are entering the RAS and WAS streams. As WAS leaves the PFR and is sent through the digesters and then to the front of the plant, the high concentrations at lower rates cause the primary clarifier to spike (Figure 5-97).

Figure 5-99: MBR Filtrate VSS and Xa with Varying MBR WAS

The membrane in the MBR largely removes VSS and Xa (Figure 5-99). The filtrate concentrations are within the same order of magnitude as the plant effluent concentrations when the PFR is used. Because filtrate concentrations are so low, the secondary clarifier is now essentially a polishing clarifier (Figure 5-100).

Figure 5-100: Effluent VSS and Xa with Varying MBR WAS

Due to the increased concentrations of VSS and Xa in primary clarifiers, CECs experience higher removal in the primary clarifiers as WAS increases (Figure 5-101). Removal patterns in the primary clarifiers are similar to those when PFRs are used and WAS from the secondary clarifiers increases (Figure 5-87).

Figure 5-101: Primary Clarifier CEC Removal with Varying MBR WAS

Figure 5-102: MBR CEC Removal with Varying MBR WAS

Because VSS and Xa decrease in the MBRs as WAS increases, CEC removal decreases (Figure 5-102). Iohexol and DEET experience close to 10% decrease in removal percentage, while atenolol, iopromide, and acesulfame-K about 5% change. In general, the rate at which MBR removal decreases is smaller than the rate which primary clarifier removal increases.

Finally, the overall plant removal was analyzed. Because primary clarifier removal increases and MBR removal decreases, overall removal was relatively constant (Figure 5-103). Although gradual, CECs tend to experience change in removal percentage after WAS reaches about 5%, corresponding to a SRT of about 4.5 days. Although MBR removal percentages do not fluctuate as much as primary clarifier percentages, because more removal occurs in the MBRs, plant removal change is small (only up to 3% for DEET and iohexol).

Figure 5-103: Plant CEC Removal with Varying MBR WAS

### MBR RAS Analysis

In MBRs, RAS can be as high as four times (400%) larger than the influent flow (Davis, 2010). To ensure that the optimized RAS was chosen, it was analyzed from 100 to 800% in each MBR. In the primary clarifiers, RAS has little effect on VSS and Xa concentrations (Figure 5-104).

Figure 5-104: Primary Clarifier VSS and Xa with Varying RAS

Unlike in varying WAS analysis, VSS and Xa concentrations in each MBR chamber display different patterns as RAS increases. While VSS and Xa in the first two chambers increase with increasing RAS, concentrations in the third chamber decreased (Figure 5-105). Because RAS is pumped from the last chamber to the first, as RAS increases, a higher mass loading is sent from the effluent to the MBR to the influent. While this decreases concentrations in the third chamber, it increases concentrations in the first and second.

Figure 5-105: MBR VSS and Xa with Varying RAS

Similar to the primary clarifiers, RAS has little effect on filtrate and plant effluent concentrations. Furthermore, because the membrane treats the water to low VSS and Xa concentrations, the secondary clarifier acts only as a polishing tank, without significant removal (Figure 5-106 to Figure 5-107).

Figure 5-106: MBR Filtrate VSS and Xa with Varying RAS

Figure 5-107: Effluent VSS and Xa with Varying RAS

Due to the small change in removal percentages in the primary clarifiers and MBRs, CEC data is not shown. In both, CEC removal slightly decreases as RAS increases. The same is true for overall plant removal. Although the change is small, as RAS increases, CEC removal decreases (Figure 5-108).

Figure 5-108: Plant CEC Removal with Varying RAS

At lower RAS rates, CEC removal increases at a larger rate than it does as RAS approaches 800% (Figure 5-108). Regardless of the removal percentage, each CEC tends to decrease in removal percentage at relatively the same rate. As with the expanded model RAS, there is a balance between other constituents and CECs. As RAS increases, plant effluent VSS and Xa decrease but CEC concentrations increase. However, the change in removal percentage is small (<3% for most CECs) even as RAS approaches 800%.

## Expanded and Advanced Model Comparisons

After sensitivity analyses were completed for the enhanced and advanced models, the two were compared to determine the improvement of MBRs in the removal of CECs at the NWRF. First, using these analyses, optimized WAS and RAS rates were determined for each model. These rates (shown below) were selected based on CEC removal as well as effluent VSS and Xa concentrations, attempting to find a balance between the parameters. The optimized parameters are as follows:

- Expanded model:

  - Primary Clarifier WAS: 0.1%

  - Secondary Clarifier WAS: 4%

  - RAS: 70%

- Advanced model:

  - Primary Clarifier WAS: 0.1%

  - Secondary Clarifier WAS: 4%

  - MBR WAS: 5%

  - RAS: 200%

With these parameters, the models were compared using sampling data (with modified flowrate). First, VSS and Xa concentrations were analyzed throughout the plant (Figure 5-109). The expanded model has larger concentrations of VSS and Xa in the preliminary and primary clarifier effluents. Secondary clarifier WAS is less concentrated in the advanced model because of the high removal from the membrane in the MBR. For this reason, because WAS is eventually returned to the front of the NWRF, preliminary and primary clarifier effluent VSS and Xa concentrations are lower in the advanced model. However, as mentioned, even when WAS approached 0%, there was not a significant increase in VSS or Xa concentrations (Figure 5-103).

Figure 5-109: Preliminary and Primary Clarifier Advanced vs. Expanded Xa and VSS under Sampling Conditions (Modified Flowrate)

Next, VSS and Xa were analyzed in the PFR, MBR, and plant effluents. While expanded model concentrations are relatively stable throughout the PFR, concentrations in the MBR (advanced model) increase by chamber. The averages of the three chambers for VSS and Xa in both models are:

- Advanced model Xa: 2820 mg/L

- Advanced model VSS: 4393.33 mg/L

- Expanded model Xa: 2646.67 mg/L

- Expanded model VSS: 3360 mg/L

There is just a small difference in the Xa concentrations between the advanced and expanded models. The advanced model VSS concentration, meanwhile, is about 30% larger than the expanded model.

Although it is difficult to tell in the graph, expanded model plant effluent VSS and Xa concentrations are approximately ten times larger than concentrations in the advanced model (Figure 5-110). This can be attributed to the membrane, which removes VSS and Xa to concentrations of less than 1 mg/L.

Figure 5-110: MBR or PFR Advanced vs. Expanded Xa and VSS under Sampling Conditions (Modified Flowrate)

Because of the higher concentrations of VSS and Xa in the primary clarifiers, the expanded model primary clarifiers typically remove CECs slightly better than the advanced model primary clarifiers. PFR and MBR removal percentages are similar for the two models. Despite the higher levels of Xa in the MBRs, CEC removal does not change significantly (Figure 5-111 to Figure 5-122).

Figure 5-111: Expanded vs. Advanced Meprobamate under Sampling Conditions (Modified Flowrate)

Figure 5-112: Expanded vs. Advanced Triclosan under Sampling Conditions (Modified Flowrate)

Figure 5-113: Expanded vs. Advanced Atenolol under Sampling Conditions (Modified Flowrate)

Figure 5-114: Expanded vs. Advanced E1 under Sampling Conditions (Modified Flowrate)

Figure 5-115: Expanded vs. Advanced Gemfibrozil under Sampling Conditions (Modified Flowrate)

Figure 5-116: Expanded vs. Advanced DEET under Sampling Conditions (Modified Flowrate)

Figure 5-117: Expanded vs. Advanced Caffeine under Sampling Conditions (Modified Flowrate)

Figure 5-118: Expanded vs. Advanced Theobromine under Sampling Conditions (Modified Flowrate)

Figure 5-119: Expanded vs. Advanced Sucralose under Sampling Conditions (Modified Flowrate)

Figure 5-120: Expanded vs. Advanced Acesulfame-K under Sampling Conditions (Modified Flowrate)

Figure 5-121: Expanded vs. Advanced Iopromide under Sampling Conditions (Modified Flowrate)

Figure 5-122: Expanded vs. Advanced Iohexol under Sampling Conditions (Modified Flowrate)

There is no significant difference in CEC removal between the expanded and advanced models. In the MBR membranes, GPS-X only removes soluble compounds when they are inert. Because the CECs are not inert in the model, they are not removed by the membrane. For micro- and ultrafiltration membranes, pore size is on the order of 100 times larger than most CECs. However, some removal may take place due to sorption to the membrane (Lee et al., 2009). Therefore, although removal varies, actual CEC concentrations might be expected to be lower than levels determined in the advanced model.

While modeled soluble CECs are not shown to decrease through the membrane, advanced model particulate CECs are removed to lower concentrations than expanded model concentrations. Although effluent particulate CEC concentrations in the expanded model are small, advanced model filtrate and plant concentrations are approximately ten times smaller. Even without the secondary clarifiers, the advanced model is still better at removing particulate CECs (Figure 5-123 to Figure 5-134).

Figure 5-123: Expanded vs. Advanced Particulate Meprobamate under Sampling Conditions (Modified Flowrate)

Figure 5-124: Expanded vs. Advanced Particulate Triclosan under Sampling Conditions (Modified Flowrate)

Figure 5-125: Expanded vs. Advanced Particulate Atenolol under Sampling Conditions (Modified Flowrate)

Figure 5-126: Expanded vs. Advanced Particulate E1 under Sampling Conditions (Modified Flowrate)

Figure 5-127: Expanded vs. Advanced Particulate Gemfibrozil under Sampling Conditions (Modified Flowrate)

Figure 5-128: Expanded vs. Advanced Particulate DEET under Sampling Conditions (Modified Flowrate)

Figure 5-129: Expanded vs. Advanced Particulate Caffeine under Sampling Conditions (Modified Flowrate)

Figure 5-130: Expanded vs. Advanced Particulate Theobromine under Sampling Conditions (Modified Flowrate)

Figure 5-131: Expanded vs. Advanced Particulate Sucralose under Sampling Conditions (Modified Flowrate)

Figure 5-132: Expanded vs. Advanced Particulate Acesulfame-K under Sampling Conditions (Modified Flowrate)

Figure 5-133: Expanded vs. Advanced Particulate Iopromide under Sampling Conditions (Modified Flowrate)

Figure 5-134: Expanded vs. Advanced Particulate Iohexol under Sampling Conditions (Modified Flowrate)

Next, soluble CEC data was extrapolated to analyze concentrations throughout an entire year. Again, influent data (except an increased flowrate) from 2013 was used as the influent data in the extrapolated advanced model. Flowrate, as mentioned earlier, is 75% higher than the base model flowrate. Both the advanced and expanded CEC concentrations are graphed (Figure 5-135 to Figure 5-146). The expanded model typically outperforms the advanced model for CEC removal. However, as mentioned, GPS-X does not account for removal of soluble CECs in the membrane. Therefore, advanced model concentrations could be expected to be lower than model prediction.

Figure 5-135: Expanded vs. Advanced Extrapolated Meprobamate

Figure 5-136: Expanded vs. Advanced Extrapolated Triclosan

Figure 5-137: Expanded vs. Advanced Extrapolated Atenolol

Figure 5-138: Expanded vs. Advanced Extrapolated E1

Figure 5-139: Expanded vs. Advanced Extrapolated Gemfibrozil

Figure 5-140: Expanded vs. Advanced Extrapolated DEET

Figure 5-141: Expanded vs. Advanced Extrapolated Caffeine

Figure 5-142: Expanded vs. Advanced Extrapolated Theobromine

Figure 5-143: Expanded vs. Advanced Extrapolated Sucralose

Figure 5-144: Expanded vs. Advanced Extrapolated Acesulfame-K

Figure 5-145: Expanded vs. Advanced Extrapolated Iopromide

Figure 5-146: Expanded vs. Advanced Extrapolated Iohexol

CECs that rely on biodegradation for removal (atenolol, DEET, caffeine, theobromine, and iohexol) typically perform equally in the advanced and expanded models. As mentioned earlier, meprobamate, gemfibrozil, and sucralose rate constants were only calibrated for the primary clarifiers.  These compounds, though, are typically less removed in the advanced model due to their dependence on adsorption. These trends show the importance of biodegradation in the advanced model. Because VSS concentrations are lower (Figure 5-109), the advanced model relies more heavily on biodegradation.

# Conclusion

With the rise in popularity of direct and indirect water reuse, CECs are of growing concern to both ecosystems and human consumption. Because direct and indirect reuse can include wastewater effluent application to natural streams, lakes, irrigated land, and even water treatment plants, it is desirable to understand CEC concentrations and removal patterns throughout WWTPs. Due to the wide range of WWTP characteristics, CEC removal varies greatly and can be difficult to predict without knowledge and information of the specific plant. This research uses a stochastic model to analyze CEC removal through the various treatment processes at the NWRF. Using the commercial software GPS-X, CECs are analyzed with varying RAS, WAS, SRTs, and HRTs. GPS-X incorporates the use of the model developer tool, which uses matrix format to model the relationships between model parameters and CECs that are added to the model. This research evaluates operational effects at the NWRF on CEC removal. Additionally, it analyzes the use of MBRs instead of PFRs and evaluates advanced treatment options for CEC removal.

CECs are primarily removed from wastewater by biodegradation and adsorption to biosolids. At low CEC concentrations, both biodegradation and adsorption are first-order reactions with respect to Xa and VSS concentrations, respectively. While most reclamation facilities use CAS, other treatment techniques include MBRs, RO and other membrane processes, and UV disinfection. In the NWRF, CECs are most significantly removed in the primary clarifiers and the PFR. Because of the high concentrations of Xa and VSS, these treatment processes are able to remove CECs. Of 98 CECs analyzed, only 38 are larger than the MRL in one or more of the treatment processes. Furthermore, influent and effluent indicator CEC concentrations are well below MTT levels. There are some general trends from biodegradation and adsorption that can be seen from CEC removal:

- CECs that are predominantly removed in the PFR (caffeine, theobromine, iopromide, and acesulfame-K) are heavily biodegraded in the PFR and experience removal from both biodegradation and adsorption in the primary clarifiers. These CECs have the highest removal percentages (>94%) of all indicator and validator CECs in the study.

- CECs that are mostly removed in the primary clarifiers (sucralose, meprobamate, and gemfibrozil) rely on adsorption in both the primary clarifiers and the PFR. These CECs have the lowest removal percentages (<30%) of modeled CECs in the NWRF.

- CECs that show steady and equal removal through both the primary clarifiers and the PFR (atenolol, iohexol, DEET) tend to favor biodegradation in both treatment processes. These CECs have removal percentages between 39 and 91% from the NWRF.

RAS and WAS are operational effects that can help reduce CEC concentrations in WWTPs. However, as with most engineered processes, there is a balance between CEC concentrations and plant performance for others contaminants. As mentioned, biodegradation and adsorption are first-order rates with respect to Xa and VSS. Therefore, at higher levels of Xa and VSS, CEC removal rates increase. RAS has varying effects on removal. While some CECs experience increased removal with increasing RAS, other CECs decrease in removal. CECs that rely more heavily on biodegradation for removal tend to increase in removal percentage as RAS increases. However, RAS has a small effect on overall CEC removal, with each CEC experiencing less than 4% change in removal percentage.

Because it controls SRT, secondary clarifier WAS has a larger effect on CEC removal than RAS. Interestingly, there seems to be a clear critical point with WAS flowrate. As WAS approaches 4 to 5%, removal percentage of each CEC is optimized. This confirms current literature (Clara et al., 2005a; Monteith et al., 2008; Jelić et al., 2012) that suggests that critical SRT (and consequentially WAS) can be determined to optimize CEC removal. In these studies, as SRT increases, CEC removal increases but generally reaches a maximum percentage. In the model, at this critical WAS, plant effluent VSS and Xa reach a low point and are maintained with increasing WAS. Unlike RAS, there is a clear optimum WAS rate in which CEC removal is maximized and plant effluent VSS and Xa are minimized. For these reasons, adjustment of the secondary clarifier WAS is a more viable operational change to the NWRF for CEC removal.

In GPS-X, MBRs do not significantly increase soluble removal percentages of any of the CECs modeled. However, because of the membrane filter, particulate CECs are removed approximately ten times greater in the MBRs than they are in the PFRs and secondary clarifiers of the expanded model. Although particulate removal depends on the membrane used, Clara et al. (2005b) and Radjenović et al. (2006) confirm that particulate matter is detained by an ultrafiltration membrane, resulting in negligible concentrations of suspended solids in the effluent.  In this research, modeled MBR filtrate VSS and Xa concentrations are also about ten times smaller than expanded model plant effluent concentrations, eliminating the need for the secondary clarifiers.

Changes in WAS or RAS in the MBRs did not show a large effect on modeled CEC removal. In contrast, literature finds that increased SRT (decreased WAS) increases CEC removal. Longer SRTs result in diversified biomass, allowing for higher removal (Kimura et al., 2007; Radjenović et al., 2009). This research did not account for biomass diversification, which could be a reason that increased SRTs only slightly increase CEC removal. Although GPS-X does not show the removal of soluble CECs with the membrane, several studies (Kimura et al., 2005; Lee et al., 2009; Sipma et al., 2010; Snyder et al., 2007) show that CEC removal is a function of the type of membrane used, pressure, flux, and molecular weight of the CEC. Furthermore, UV disinfection removal depends on intensity-time values and can be as large as 90% (Canonica et al., 2008; Kim et al., 2009). So, although modeled MBR removal is similar to PFR removal, AT techniques, if properly applied, can help to remove CECs in WWTPs. This is in agreement with literature information, confirming that AT processes can increase CEC removal when compared to CAS systems.

As mentioned, both influent and effluent CEC concentrations in the NWRF are below MTT levels. The models in this research suggest that the plant expansion (even with increased flowrate) might slightly decrease removal percentages of CECs, but not at a level that should cause concern. If concentrations do rise to levels approaching the MTT, WAS could be an effective parameter to increase removal percentage of the overall plant. Several studies (Clara et al., 2005a; Monteith et al., 2008; Jelić et al., 2012) show that determining critical SRT (which is controlled by WAS) can enhance CEC removal in CAS systems. MBRs, though, have the potential to increase removal percentage greater than operational changes can. As mentioned, CECs that are sorbed to biomass (particulate CECs) can be expected to be smaller in effluent concentrations if MBRs are utilized. Furthermore, research suggests that soluble CECs can experience higher removal depending on the type of membrane used.

The following is a summary of limitations that are also noted throughout the paper:

- CECs were only collected during one sampling day. In order to better evaluate removal, more data from various months of the year is desirable.

- CEC analysis did not indicate whether the CEC was ionized or neutral. This could have some effect on removal in the plant.

- GPS-X, while extensive and robust for suspended and attached growth processes, does not allow for the modeling of some AT processes, like UV disinfection and membrane filtration. Furthermore, CEC removal mechanisms are not able to be modeled in the digesters.

- MBR membranes do not remove soluble matter in GPS-X. The model does not allow for the input of size, pressure, or other characteristics needed for membrane filtration.

Based on the mentioned limitations and on the research as a whole, the following recommendations are made:

- If possible, more sampling should be completed. Seasonal and even daily variations of CECs are possible and more data would allow for a more finely calibrated mode.

- Because of the lack of model capability for AT processes and the wide range of removal percentages, pilot or bench-scale testing is likely the most ideal option for understanding removal through AT processes.

- In CAS processes, sampling and analysis of CECs only in the primary clarifiers and PFRs can save time and money. These unit processes account for the majority of removal in CAS WWTPs.

As direct and indirect water reuse becomes increasingly popular, information regarding CEC removal in WWTPs is needed. This research helps to understand CEC removal in the NWRF. Using a stochastic model, it is able to evaluate and quantify the key removal mechanisms in CAS treatment processes, operational improvements to increase CEC removal, and the use and benefit of AT processes in WWTPs.

# References

Alan Plummer Associates, Incorporated. “Direct Potable Reuse Resource Document.” Texas Water Development Board, April 2015. http://www.twdb.texas.gov/publications/reports/contracted_reports/doc/1248321508_Vol1.pdf.

Asano, Yasuhisa, Toshihiro Komeda, and Hideaki Yamada. “Microbial Production of Theobromine from Caffeine.” Bioscience, Biotechnology, and Biochemistry 57, no. 8 (January 1, 1993): 1286–89. doi:10.1271/bbb.57.1286.

Bernhard, Marco, Jutta Müller, and Thomas P. Knepper. “Biodegradation of Persistent Polar Pollutants in Wastewater: Comparison of an Optimised Lab-Scale Membrane Bioreactor and Activated Sludge Treatment.” Water Research 40, no. 18 (October 2006): 3419–28. doi:10.1016/j.watres.2006.07.011.

Blair, Benjamin, Adam Nikolaus, Curtis Hedman, Rebecca Klaper, and Timothy Grundl. “Evaluating the Degradation, Sorption, and Negative Mass Balances of Pharmaceuticals and Personal Care Products during Wastewater Treatment.” Chemosphere 134 (September 2015): 395–401. doi:10.1016/j.chemosphere.2015.04.078.

Canonica, Silvio, Laurence Meunier, and Urs von Gunten. “Phototransformation of Selected Pharmaceuticals during UV Treatment of Drinking Water.” Water Research 42, no. 1–2 (January 2008): 121–28. doi:10.1016/j.watres.2007.07.026.

Carballa, Marta, Guido Fink, Francisco Omil, Juan M. Lema, and Thomas Ternes. “Determination of the Solid–water Distribution Coefficient (Kd) for Pharmaceuticals, Estrogens and Musk Fragrances in Digested Sludge.” Water Research 42, no. 1–2 (January 2008): 287–95. doi:10.1016/j.watres.2007.07.012.

Clara, M., B. Strenn, M. Ausserleitner, and N. Kreuzinger. “Comparison of the Behaviour of Selected Micropollutants in a Membrane Bioreactor and a Conventional Wastewater Treatment Plant.” Water Science and Technology: A Journal of the International Association on Water Pollution Research 50, no. 5 (2004): 29–36.

Clara, M., N. Kreuzinger, B. Strenn, O. Gans, and H. Kroiss. “The Solids Retention Time—a Suitable Design Parameter to Evaluate the Capacity of Wastewater Treatment Plants to Remove Micropollutants.” Water Research 39, no. 1 (January 2005a): 97–106. doi:10.1016/j.watres.2004.08.036.

Clara, M., B. Strenn, O. Gans, E. Martinez, N. Kreuzinger, and H. Kroiss. “Removal of Selected Pharmaceuticals, Fragrances and Endocrine Disrupting Compounds in a Membrane Bioreactor and Conventional Wastewater Treatment Plants.” Water Research 39, no. 19 (November 2005b): 4797–4807. doi:10.1016/j.watres.2005.09.015.

Davis, Mackenzie. Water and Wastewater Engineering Design Principles and Practice. 1st ed. McGraw-Hill Professional, 2010.

Ghalajkhani, Rosita. “Fate Modeling of Xenobiotic Organic Compounds (XOCs) in Wastewater Treatment Plants,” November 15, 2013.https://uwspace.uwaterloo.ca/handle/10012/8037.

Githinji, Leonard J. M., Michael K. Musey, and Ramble O. Ankumah. “Evaluation of the Fate of Ciprofloxacin and Amoxicillin in Domestic Wastewater.” Water, Air, & Soil Pollution 219, no. 1–4 (November 26, 2010): 191–201. doi:10.1007/s11270-010-0697-1.

Gun’ko, V. M. “Competitive Adsorption.” Theoretical and Experimental Chemistry 43, no. 3 (May 2007): 139–83. doi:10.1007/s11237-007-0020-4.

Hydromantis. “Model Developer GPS-X 6.4,” November 17, 2014.

Hyland, Katherine. “Sorption and Bioaccumulation of Neutral and Ionizable Wastewater-Derived Contaminants of Emerging Concern: Exposure of Edible Crops via Solid and Liquid Effluent Streams.” Colorado School of Mines, 2014. http://dspace.library.colostate.edu/webclient/DeliveryManager/digitool_items/csm01_storage/2014/10/06/file_1/342128.

Jelić, Aleksandra, Meritxell Gros, Mira Petrović, Antoni Ginebreda, and Damià Barceló. “Occurrence and Elimination of Pharmaceuticals During Conventional Wastewater Treatment.” In Emerging and Priority Pollutants in Rivers, edited by Helena Guasch, Antoni Ginebreda, and Anita Geiszinger, 1–23. The Handbook of Environmental Chemistry 19. Springer Berlin Heidelberg, 2012.http://link.springer.com/chapter/10.1007/978-3-642-25722-3_1.

Johnson, A. C., H. -R. Aerni, A. Gerritsen, M. Gibert, W. Giger, K. Hylland, M. Jürgens, et al. “Comparing Steroid Estrogen, and Nonylphenol Content across a Range of European Sewage Plants with Different Treatment and Management Practices.” Water Research 39, no. 1 (January 2005): 47–58. doi:10.1016/j.watres.2004.07.025.

Jones, O. A. H, N Voulvoulis, and J. N Lester. “Aquatic Environmental Assessment of the Top 25 English Prescription Pharmaceuticals.” Water Research 36, no. 20 (December 2002): 5013–22. doi:10.1016/S0043-1354(02)00227-0.

Joss, Adriano, Henrik Andersen, Thomas Ternes, Philip R. Richle, and Hansruedi Siegrist. “Removal of Estrogens in Municipal Wastewater Treatment under Aerobic and Anaerobic Conditions:  Consequences for Plant Optimization. “Environmental Science & Technology 38, no. 11 (June 1, 2004): 3047–55. doi:10.1021/es0351488.

Joss, Adriano, Sebastian Zabczynski, Anke Göbel, Burkhard Hoffmann, Dirk Löffler, Christa S. McArdell, Thomas A. Ternes, Angela Thomsen, and Hansruedi Siegrist. “Biological Degradation of Pharmaceuticals in Municipal Wastewater Treatment: Proposing a Classification Scheme. “Water Research 40, no. 8 (May 2006): 1686–96. doi:10.1016/j.watres.2006.02.014.

Kim, Ilho, Naoyuki Yamashita, and Hiroaki Tanaka. “Photodegradation of Pharmaceuticals and Personal Care Products during UV and UV/H2O2 Treatments.” Chemosphere 77, no. 4 (October 2009): 518–25. doi:10.1016/j.chemosphere.2009.07.041.

Kimura, Katsuki, Shiho Toshima, Gary Amy, and Yoshimasa Watanabe. “Rejection of Neutral Endocrine Disrupting Compounds (EDCs) and Pharmaceutical Active Compounds (PhACs) by RO Membranes.” Journal of Membrane Science 245, no. 1–2 (December 1, 2004): 71–78. doi:10.1016/j.memsci.2004.07.018.

Kimura, Katsuki, Hiroe Hara, and Yoshimasa Watanabe. “Removal of Pharmaceutical Compounds by Submerged Membrane Bioreactors (MBRs).” Desalination, Membranes in Drinking and Industrial Water Production, 178, no. 1–3 (July 10, 2005): 135–40. doi:10.1016/j.desal.2004.11.033.

Kimura, Katsuki, Hiroe Hara, and Yoshimasa Watanabe. “Elimination of Selected Acidic Pharmaceuticals from Municipal Wastewater by an Activated Sludge System and Membrane Bioreactors.” Environmental Science & Technology 41, no. 10 (May 2007): 3708–14. doi:10.1021/es061684z.

Lee, C.O., K.J. Howe, and B.M. Thomson. “State of Knowledge of Pharmaceutical, Personal Care Product, and Endocrine Disrupting Compound Removal During Wastewater Treatment.” Final Report. Albuquerque, NM: The University of New Mexico, April 2009. http://www.unm.edu/~howe/UNM20Howe20PPCP20Final20Report.pdf

Lee, Do Gyun, Fuman Zhao, Yohannes H. Rezenom, David H. Russell, and Kung-Hui Chu. “Biodegradation of Triclosan by a Wastewater Microorganism.” Water Research 46, no. 13 (September 1, 2012): 4226–34. doi:10.1016/j.watres.2012.05.025.

Lishman, Lori, Shirley Anne Smyth, Kurtis Sarafin, Sonya Kleywegt, John Toito, Thomas Peart, Bill Lee, Mark Servos, Michel Beland, and Peter Seto. “Occurrence and Reductions of Pharmaceuticals and Personal Care Products and Estrogens by Municipal Wastewater Treatment Plants in Ontario, Canada.” Science of The Total Environment 367, no. 2–3 (August 31, 2006): 544–58. doi:10.1016/j.scitotenv.2006.03.021.

Luo, Yunlong, Wenshan Guo, Huu Hao Ngo, Long Duc Nghiem, Faisal Ibney Hai, Jian Zhang, Shuang Liang, and Xiaochang C. Wang. “A Review on the Occurrence of Micropollutants in the Aquatic Environment and Their Fate and Removal during Wastewater Treatment.” Science of The Total Environment 473–74 (March 1, 2014): 619–41. doi:10.1016/j.scitotenv.2013.12.065.

Maurer, M., B. I. Escher, P. Richle, C. Schaffner, and A. C. Alder. “Elimination of β-Blockers in Sewage Treatment Plants.” Water Research 41, no. 7 (April 2007): 1614–22. doi:10.1016/j.watres.2007.01.004.

Meyer, J., and K. Bester. “Organophosphate Flame Retardants and Plasticisers in Wastewater Treatment Plants.” Journal of Environmental Monitoring 6, no. 7 (July 2, 2004): 599–605. doi:10.1039/B403206C.

Miège, C., J. M. Choubert, L. Ribeiro, M. Eusèbe, and M. Coquery. “Removal Efficiency of Pharmaceuticals and Personal Care Products with Varying Wastewater Treatment Processes and Operating Conditions – Conception of a Database and First Results.” Water Science & Technology 57, no. 1 (January 2008): 49. doi:10.2166/wst.2008.823.

Monteith, Hugh, Hank Andres, Spencer Snowling, and Oliver Schraa. “Modeling the Fate of Estrogenic Hormones in Municipal Wastewater Treatment.” Proceedings of the Water Environment Federation 2008, no. 13 (January 1, 2008): 3477-95.

Okuda, Takashi, Naoyuki Yamashita, Hiroaki Tanaka, Hiroshi Matsukawa, and Kaoru Tanabe. “Development of Extraction Method of Pharmaceuticals and Their Occurrences Found in Japanese Wastewater Treatment Plants.” Environment International, Pharmaceutical products in the environment: trends toward lowering presence and impact, 35, no. 5 (July 2009): 815–20. doi:10.1016/j.envint.2009.01.006.doi:10.2175/193864708788733134.

Osachoff, Heather L., Mehrnoush Mohammadali, Rachel C. Skirrow, Eric R. Hall, Lorraine L. Y. Brown, Graham C. van Aggelen, Christopher J. Kennedy, and Caren C. Helbing. “Evaluating the Treatment of a Synthetic Wastewater Containing a Pharmaceutical and Personal Care Product Chemical Cocktail: Compound Removal Efficiency and Effects on Juvenile Rainbow Trout. “Water Research 62 (October 1, 2014): 271–80. doi:10.1016/j.watres.2014.05.057.

Schraa, Oliver, Paul Robinson, and Anette Selegran. “Modeling of an IFAS Process with Fungal Biomass Treating Pharmaceutical Wastewater.” Hamilton, ON, Canada, 2006.

Shraim, Amjad, Atef Diab, Awadh Alsuhaimi, Esmail Niazy, Mohammed Metwally, Maan Amad, Salim Sioud, and Abdulilah Dawoud. “Analysis of Some Pharmaceuticals in Municipal Wastewater of Almadinah Almunawarah.” Arabian Journal of Chemistry. (November 2012). doi:10.1016/j.arabjc.2012.11.014.

Sipma, Jan, Begoña Osuna, Neus Collado, Hector Monclús, Giuliana Ferrero, Joaquim Comas, and Ignasi Rodriguez-Roda. “Comparison of Removal of Pharmaceuticals in MBR and Activated Sludge Systems.” Desalination 250, no. 2 (January 15, 2010): 653–59. doi:10.1016/j.desal.2009.06.073.

Snyder, Shane A., Samer Adham, Adam M. Redding, Fred S. Cannon, James DeCarolis, Joan Oppenheimer, Eric C. Wert, and Yeomin Yoon. “Role of Membranes and Activated Carbon in the Removal of Endocrine Disruptors and Pharmaceuticals.” Desalination, Wastewater Reclamation and Reuse for Sustainability, 202, no. 1–3 (January 5, 2007): 156–81. doi:10.1016/j.desal.2005.12.052.

Stevens-Garmon, John, Jörg E. Drewes, Stuart J. Khan, James A. McDonald, and Eric R. V. Dickenson. “Sorption of Emerging Trace Organic Compounds onto Wastewater Sludge Solids.” Water Research, no. 11 (May 2011): 3417–26. doi:10.1016/j.watres.2011.03.056.

Radjenović, Jelena, Mira Petrović, and Damià Barceló. “Analysis of Pharmaceuticals in Wastewater and Removal Using a Membrane Bioreactor.” Analytical and Bioanalytical Chemistry 387, no. 4 (November 18, 2006): 1365–77. doi:10.1007/s00216-006-0883-6.

Radjenović, Jelena, Mira Petrović, and Damià Barceló. “Fate and Distribution of Pharmaceuticals in Wastewater and Sewage Sludge of the Conventional Activated Sludge (CAS) and Advanced Membrane Bioreactor (MBR) Treatment.” Water Research 43, no. 3 (February 2009): 831–41. doi:10.1016/j.watres.2008.11.043.

Reungoat, J., B. I. Escher, M. Macova, and J. Keller. “Biofiltration of Wastewater Treatment Plant Effluent: Effective Removal of Pharmaceuticals and Personal Care Products and Reduction of Toxicity.” Water Research 45, no. 9 (April 2011): 2751–62. doi:10.1016/j.watres.2011.02.013.

Rittmann, Bruce E., and Perry L. McCarty. Environmental Biotechnology: Principles and Applications. McGraw-Hill, 2001.

Ternes, Thomas A., Nadine Herrmann, Matthias Bonerz, Thomas Knacker, Hansruedi Siegrist, and Adriano Joss. “A Rapid Method to Measure the Solid–water Distribution Coefficient (Kd) for Pharmaceuticals and Musk Fragrances in Sewage Sludge.” Water Research 38, no. 19 (November 2004): 4075–84. doi:10.1016/j.watres.2004.07.015.

Tran, Ngoc Han, Jie Gan, Viet Tung Nguyen, Huiting Chen, Luhua You, Ankur Duarah, Lifeng Zhang, and Karina Yew-Hoong Gin. “Sorption and Biodegradation of Artificial Sweeteners in Activated Sludge Processes.” Bioresource Technology 197 (December 2015): 329–38. doi:10.1016/j.biortech.2015.08.083.

Urase, Taro, and Tomoya Kikuta. “Separate Estimation of Adsorption and Degradation of Pharmaceutical Substances and Estrogens in the Activated Sludge Process.” Water Research 39, no. 7 (April 2005): 1289–1300. doi:10.1016/j.watres.2005.01.015.

US EPA. “Wastewater Management Fact Sheet: Membrane Bioreactors,” September 2007. http://water.epa.gov/scitech/wastetech/upload/2008_01_23_mtb_etfs_membrane-bioreactors.pdf.

US EPA, OW. “Contaminants of Emerging Concern,” May 8, 2014. http://water.epa.gov/scitech/cec/

Verlicchi, P., M. Al Aukidy, and E. Zambello. “Occurrence of Pharmaceutical Compounds in Urban Wastewater: Removal, Mass Load and Environmental Risk after a Secondary treatment—A Review.” Science of The Total Environment, Special Section - Arsenic in Latin America, An Unrevealed Continent: Occurrence, Health Effects and Mitigation, 429 (July 1, 2012): 123–55. doi:10.1016/j.scitotenv.2012.04.028.

Wang, Dan, Qian Sui, Shu-Guang Lu, Wen-Tao Zhao, Zhao-Fu Qiu, Zhou-Wei Miao, and Gang Yu. “Occurrence and Removal of Six Pharmaceuticals and Personal Care Products in a Wastewater Treatment Plant Employing Anaerobic/anoxic/aerobic and UV Processes in Shanghai, China.” Environmental Science and Pollution Research 21, no. 6 (December 5, 2013): 4276–85. doi:10.1007/s11356-013-2363-9.

Wick, Arne, Guido Fink, Adriano Joss, Hansruedi Siegrist, and Thomas A. Ternes. “Fate of Beta Blockers and Psycho-Active Drugs in Conventional Wastewater Treatment.” Water Research 43, no. 4 (March 2009): 1060–74. doi:10.1016/j.watres.2008.11.031.

# Appendix A: NWRF Typical Wastewater Parameters

| Date | Flow (MGD) | Infl. Temp. (°C) | Infl. pH | Infl. TSS (mg/L) | Infl. cBOD5 (mg/L) | Infl. NH3-N (mg/L) | Infl. DO (mg/L) | Effl. Temp. (°C) | Effl. pH | Effl. TSS (mg/L) | Effluent cBOD5 (mg/L) | Effl. NH3-N (mg/L) | Effl. DO (mg/L) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1/1/12 | 8.445 | 18.2 | 7.4 | 164 | 265 | 27.8 | 1.2 | 17.8 | 7.2 | 7 | 3 | 1.1 | 7.2 |
| 1/2/12 | 9.033 | 15.6 | 7.5 | 208 | 253 |  | 1.5 | 15.0 | 7.3 | 5 | 2 |  | 6.5 |
| 1/3/12 | 8.968 | 15.5 | 7.6 | 136 | 232 |  | 1.3 | 15.0 | 7.2 | 4 | 2 | 0.1 | 6.4 |
| 1/4/12 | 8.842 | 15.7 | 7.7 | 112 | 214 |  | 1.4 | 14.9 | 7.3 | 20 | 4 |  | 6.3 |
| 1/5/12 | 8.867 | 15.8 | 7.6 | 156 | 222 | 26.7 | 1.5 | 15.5 | 7.3 | 4 | 2 | 0.1 | 6.5 |
| 1/6/12 | 8.671 | 15.8 | 7.5 |  |  |  | 1.1 | 15.7 | 7.3 |  |  |  | 6.3 |
| 1/7/12 | 8.853 | 15.2 | 7.6 |  |  |  | 1.7 | 15.3 | 7.4 |  |  |  | 7.0 |
| 1/8/12 | 9.116 | 15.4 | 7.5 | 216 | 234 | 29.8 | 1.3 | 15.4 | 7.3 | 4 | 3 | 0.4 | 6.3 |
| 1/9/12 | 8.749 | 15.5 | 7.7 | 140 | 227 |  | 1.5 | 14.8 | 7.3 | 4 | 2 |  | 6.3 |
| 1/10/12 | 8.586 | 15.3 | 7.6 | 144 | 227 |  | 1.3 | 15.0 | 7.2 | 4 | 2 | 0.2 | 6.3 |
| 1/11/12 | 8.739 | 15.8 | 7.8 | 160 | 239 |  | 1.3 | 15.3 | 7.3 | 5 | 2 |  | 6.1 |
| 1/12/12 | 8.603 | 15.0 | 7.7 | 136 | 245 | 26.6 | 1.4 | 13.1 | 7.4 | 4 | 2 | 0.6 | 6.9 |
| 1/13/12 | 8.953 | 15.3 | 7.7 |  |  |  | 1.4 | 14.3 | 7.3 |  |  |  | 6.5 |
| 1/14/12 | 8.941 | 15.1 | 7.5 |  |  |  | 1.4 | 14.9 | 7.1 |  |  |  | 6.9 |
| 1/15/12 | 8.931 | 15.1 | 7.5 | 180 | 202 | 27.6 | 1.4 | 15.1 | 7.3 | 29 | 5 | 0.2 | 6.5 |
| 1/16/12 | 9.485 | 15.3 | 7.7 | 160 | 255 |  | 1.6 | 15.5 | 7.3 | 4 | 2 |  | 6.6 |
| 1/17/12 | 9.085 | 15.4 | 7.7 | 152 | 237 |  | 1.3 | 14.2 | 7.3 | 4 | 2 | 0.1 | 6.4 |
| 1/18/12 | 9.346 | 15.4 | 7.8 | 196 | 242 |  | 1.4 | 14.6 | 7.3 | 3 | 2 |  | 6.7 |
| 1/19/12 | 9.147 | 15.8 | 7.8 | 160 | 323 | 23.6 | 1.4 | 15.0 | 7.3 | 3 | 2 | 0.1 | 6.5 |
| 1/20/12 | 9.039 | 15.7 | 7.7 |  |  |  | 1.5 | 15.2 | 7.0 |  |  |  | 6.5 |
| 1/21/12 | 8.960 | 14.6 | 7.7 |  |  |  | 1.7 | 14.0 | 7.3 |  |  |  | 6.8 |
| 1/22/12 | 9.173 | 15.0 | 7.7 | 164 | 259 | 25.7 | 1.6 | 14.7 | 7.1 | 8 | 2 | 0.1 | 6.6 |
| 1/23/12 | 9.299 | 15.1 | 7.7 | 160 | 251 |  | 2.5 | 15.0 | 7.3 | 6 | 4 |  | 6.6 |
| 1/24/12 | 9.256 | 15.3 | 7.7 | 204 | 248 |  | 1.3 | 15.0 | 7.1 | 16 | 5 | 0.7 | 6.6 |
| 1/25/12 | 14.085 | 13.6 | 7.8 | 132 | 179 |  | 2.4 | 14.1 | 7.3 | 36 | 10 |  | 6.3 |
| 1/26/12 | 10.003 | 15.1 | 7.8 | 212 | 205 | 38.8 | 1.4 | 14.3 | 7.3 | 8 | 4 | 0.1 | 6.8 |
| 1/27/12 | 10.357 | 15.1 | 7.7 |  |  |  | 1.6 | 14.8 | 7.3 |  |  |  | 6.4 |
| 1/28/12 | 10.301 | 14.0 | 7.5 |  |  |  | 1.8 | 14.5 | 7.1 |  |  |  | 6.5 |
| 1/29/12 | 9.557 | 15.4 | 7.6 | 164 | 276 | 31.0 | 1.5 | 15.1 | 7.3 | 12 | 4 | 0.1 | 6.5 |
| 1/30/12 | 9.431 | 15.2 | 7.5 | 210 | 268 |  | 1.2 | 15.3 | 7.3 | 14 | 3 |  | 6.4 |
| 1/31/12 | 9.584 | 16.0 | 7.4 | 264 | 299 |  | 1.0 | 16.0 | 7.3 | 16 | 4 | 0.1 | 5.9 |
| 2/1/12 | 9.040 | 15.8 | 7.7 | 164 | 261 |  | 1.0 | 15.7 | 7.2 | 18 | 4 |  | 6.1 |
| 2/2/12 | 9.045 | 15.8 | 7.7 | 144 | 238 | 29.4 | 1.2 | 15.5 | 7.3 | 6 | 2 | 0.1 | 6.7 |
| 2/3/12 | 9.665 | 15.7 | 7.5 |  |  |  | 0.9 | 15.9 | 7.3 |  |  |  | 6.7 |
| 2/4/12 | 9.177 | 14.7 | 7.6 |  |  |  | 1.2 | 14.6 | 7.5 |  |  |  | 6.9 |
| 2/5/12 | 9.392 | 15.1 | 7.6 | 172 | 240 | 28.6 | 1.4 | 14.8 | 7.4 | 2 | 2 | 0.1 | 6.9 |
| 2/6/12 | 9.006 | 15.4 | 7.6 | 160 | 251 |  | 1.4 | 14.9 | 7.3 | 2 | 2 |  | 6.9 |
| 2/7/12 | 9.050 | 15.7 | 7.7 | 164 | 235 |  | 1.5 | 15.2 | 7.2 | 2 | 2 | 0.1 | 6.6 |
| 2/8/12 | 9.005 | 15.1 | 7.7 | 156 | 218 |  | 1.6 | 14.3 | 7.2 | 2 | 2 |  | 6.8 |
| 2/9/12 | 8.885 | 15.1 | 7.7 | 160 | 244 | 28.9 | 1.6 | 14.2 | 7.2 | 2 | 2 | 0.1 | 6.6 |
| 2/10/12 | 9.276 | 14.8 | 7.7 |  |  |  | 1.6 | 14.4 | 7.2 |  |  |  | 7.0 |
| 2/11/12 | 9.326 | 13.8 | 7.4 |  |  |  | 1.5 | 13.0 | 7.0 |  |  |  | 6.0 |
| 2/12/12 | 9.461 | 14.2 | 7.6 | 180 | 282 | 21.1 | 1.3 | 13.1 | 7.2 | 4 | 2 | 0.1 | 6.5 |
| 2/13/12 | 9.993 | 14.0 | 7.7 | 196 | 242 |  | 1.4 | 13.0 | 7.3 | 3 | 2 |  | 6.7 |
| 2/14/12 | 9.425 | 14.6 | 7.7 | 144 | 212 |  | 1.6 | 13.7 | 7.1 | 3 | 2 | 0.1 | 6.6 |
| 2/15/12 | 9.647 | 15.0 | 7.6 | 156 | 213 |  | 1.7 | 15.2 | 7.2 | 3 | 2 |  | 6.4 |
| 2/16/12 | 9.361 | 15.1 | 7.8 | 164 | 229 | 23.0 | 1.8 | 14.9 | 7.2 | 3 | 2 | 0.1 | 7.0 |
| 2/17/12 | 9.612 | 15.0 | 7.7 |  |  |  | 1.9 | 15.0 | 7.3 |  |  |  | 6.8 |
| 2/18/12 | 9.760 | 14.3 | 7.6 |  |  |  | 1.6 | 14.7 | 7.4 |  |  |  | 6.9 |
| 2/19/12 | 9.722 | 15.1 | 7.5 | 252 | 309 | 22.4 | 1.7 | 15.5 | 7.2 | 4 | 2 | 0.1 | 6.9 |
| 2/20/12 | 9.722 | 14.8 | 7.6 | 176 | 205 |  | 1.6 | 14.4 | 7.2 | 7 | 2 |  | 6.6 |
| 2/21/12 | 9.621 | 14.9 | 7.6 | 120 | 204 |  | 1.7 | 15.0 | 7.2 | 6 | 2 | 0.3 | 6.9 |
| 2/22/12 | 9.502 | 15.3 | 7.6 | 180 | 233 |  | 1.7 | 15.4 | 7.2 | 6 | 2 |  | 6.5 |
| 2/23/12 | 9.532 | 15.4 | 7.5 | 168 | 228 | 26.6 | 1.5 | 15.8 | 7.0 | 14 | 4 | 0.1 | 6.5 |
| 2/24/12 | 9.912 | 14.7 | 7.6 |  |  |  | 1.5 | 15.0 | 7.0 |  |  |  | 6.6 |
| 2/25/12 | 9.811 | 14.9 | 7.5 |  |  |  | 2.0 | 15.3 | 7.3 |  |  |  | 6.5 |
| 2/26/12 | 9.724 | 15.4 | 7.5 | 160 | 227 | 21.9 | 1.9 | 15.4 | 7.1 | 12 | 4 | 0.2 | 7.9 |
| 2/27/12 | 9.418 | 15.4 | 7.6 | 152 | 236 |  | 1.3 | 15.1 | 7.1 | 26 | 4 |  | 6.2 |
| 2/28/12 | 9.612 | 15.4 | 7.6 | 216 | 287 |  | 1.9 | 15.6 | 7.1 | 81 | 5 | 0.5 | 6.7 |
| 2/29/12 | 9.253 | 15.8 | 7.5 | 156 | 241 |  | 1.3 | 15.9 | 7.2 | 30 | 4 |  | 5.3 |
| 3/1/12 | 9.413 | 15.9 | 7.5 | 151 | 281 | 38.6 | 1.9 | 16.1 | 7.1 | 21 | 8 | 0.8 | 6.3 |
| 3/2/12 | 9.350 | 15.4 | 7.6 |  |  |  | 1.1 | 15.5 | 7.2 |  |  |  | 6.4 |
| 3/3/12 | 9.288 | 14.9 | 7.6 |  |  |  | 1.5 | 15.0 | 7.3 |  |  |  | 6.5 |
| 3/4/12 | 9.401 | 15.9 | 7.5 | 184 | 255 | 21.7 | 1.3 | 16.1 | 7.1 | 31 | 4 | 0.1 | 6.3 |
| 3/5/12 | 9.436 | 15.7 | 7.4 | 132 | 249 |  | 1.2 | 16.0 | 7.1 | 11 | 3 |  | 6.2 |
| 3/6/12 | 9.319 | 15.5 | 7.6 | 248 | 279 |  | 1.2 | 15.6 | 7.1 | 28 | 4 | 0.1 | 6.3 |
| 3/7/12 | 9.214 | 16.2 | 7.6 | 228 | 252 |  | 1.2 | 16.3 | 7.1 | 22 | 5 |  | 6.3 |
| 3/8/12 | 9.204 | 15.0 | 7.6 | 180 | 223 | 37.1 | 1.1 | 14.3 | 7.2 | 17 | 5 | 0.1 | 6.3 |
| 3/9/12 | 9.097 | 15.7 | 7.6 |  |  |  | 1.2 | 15.1 | 7.2 |  |  |  | 6.8 |
| 3/10/12 | 9.416 | 15.3 | 7.5 |  |  |  | 1.6 | 15.5 | 7.3 |  |  |  | 6.6 |
| 3/11/12 | 13.343 | 14.4 | 7.4 | 196 | 220 | 21.9 | 1.3 | 15.0 | 7.1 | 148 | 10 | 0.3 | 5.6 |
| 3/12/12 | 11.011 | 15.9 | 7.7 | 200 | 197 |  | 1.2 | 15.7 | 7.2 | 18 | 5 |  | 6.2 |
| 3/13/12 | 10.276 | 16.0 | 7.7 | 260 | 230 |  | 1.2 | 16.8 | 7.3 | 15 | 4 | 0.1 | 6.2 |
| 3/14/12 | 10.121 | 16.1 | 7.7 | 304 | 256 |  | 1.4 | 17.0 | 7.2 | 21 | 4 |  | 6.2 |
| 3/15/12 | 10.105 | 16.3 | 7.6 | 164 | 234 | 26.4 | 1.3 | 17.5 | 7.2 | 15 | 4 | 0.5 | 6.2 |
| 3/16/12 | 10.035 | 16.5 | 7.5 |  |  |  | 1.2 | 17.7 | 7.3 |  |  |  | 6.4 |
| 3/17/12 | 9.650 | 15.0 | 7.5 |  |  |  | 1.4 | 17.0 | 7.3 |  |  |  | 6.3 |
| 3/18/12 | 9.127 | 16.0 | 7.5 | 164 | 242 | 24.8 | 1.4 | 17.0 | 7.2 | 48 | 4 | 1.0 | 6.4 |
| 3/19/12 | 17.167 | 14.5 | 7.1 | 252 | 134 |  | 0.5 | 15.3 | 7.2 | 334 | 28 |  | 5.2 |
| 3/20/12 | 19.212 | 14.7 | 7.6 | 200 | 165 |  | 3.3 | 14.6 | 7.2 | 13 | 7 | 3.6 | 5.8 |
| 3/21/12 | 14.985 | 15.0 | 7.6 | 336 | 247 |  | 1.9 | 15.2 | 7.3 | 16 | 5 |  | 6.4 |
| 3/22/12 | 14.090 | 14.5 | 7.6 | 176 | 144 | 17.2 | 1.1 | 14.9 | 7.2 | 10 | 7 | 3.3 | 6.2 |
| 3/23/12 | 12.189 | 15.4 | 7.7 |  |  |  | 1.3 | 15.7 | 7.3 |  |  |  | 6.6 |
| 3/24/12 | 10.750 | 15.1 | 7.6 |  |  |  | 1.5 | 15.2 | 7.3 |  |  |  | 6.7 |
| 3/25/12 | 11.491 | 16.1 | 7.6 | 132 | 202 | 21.6 | 1.3 | 17.8 | 7.4 | 4 | 2 | 0.1 | 6.7 |
| 3/26/12 | 11.583 | 16.7 | 7.6 | 148 | 217 |  | 1.1 | 17.4 | 7.2 | 5 | 2 |  | 6.6 |
| 3/27/12 | 11.283 | 16.9 | 7.6 | 130 | 215 |  | 1.5 | 17.8 | 7.1 | 4 | 2 | 1.2 | 6.4 |
| 3/28/12 | 11.441 | 16.4 | 7.4 | 388 | 245 |  | 0.8 | 17.5 | 7.2 | 6 | 2 |  | 6.1 |
| 3/29/12 | 11.883 | 17.2 | 7.6 | 136 | 221 | 28.4 | 1.5 | 18.0 | 7.3 | 8 | 3 | 0.4 | 6.3 |
| 3/30/12 | 14.604 | 17.2 | 7.6 |  |  |  | 1.4 | 18.1 | 7.2 |  |  |  | 6.0 |
| 3/31/12 | 9.667 | 17.1 | 7.5 |  |  |  | 1.4 | 17.1 | 7.2 |  |  |  | 6.2 |
| 4/1/12 | 9.799 | 17.5 | 7.5 | 164 | 205 | 25.6 | 1.6 | 19.0 | 7.0 | 34 | 4 | 2.0 | 6.2 |
| 4/2/12 | 9.616 | 18.8 | 7.5 | 148 | 197 |  | 1.2 | 20.0 | 7.2 | 16 | 4 |  | 5.8 |
| 4/3/12 | 11.339 | 18.1 | 7.5 | 172 | 212 |  | 1.2 | 18.6 | 7.2 | 14 | 5 | 1.7 | 6.0 |
| 4/4/12 | 10.048 | 18.5 | 7.7 | 192 | 173 |  | 1.2 | 19.0 | 7.3 | 20 | 4 |  | 6.1 |
| 4/5/12 | 9.521 | 18.4 | 7.5 | 156 | 186 | 26.7 | 1.2 | 18.8 | 7.2 | 16 | 4 | 0.3 | 6.0 |
| 4/6/12 | 9.473 | 18.3 | 7.5 |  |  |  | 0.7 | 18.8 | 7.2 |  |  |  | 6.1 |
| 4/7/12 | 9.449 | 17.2 | 7.5 |  |  |  | 1.4 | 18.5 | 7.2 |  |  |  | 6.2 |
| 4/8/12 | 9.229 | 17.5 | 7.4 | 168 | 216 | 24.6 | 1.2 | 17.8 | 7.2 | 31 | 5 | 0.2 | 5.8 |
| 4/9/12 | 9.399 | 17.8 | 7.5 | 156 | 198 |  | 1.2 | 18.3 | 7.3 | 30 | 4 |  | 5.8 |
| 4/10/12 | 9.265 | 18.0 | 7.5 | 144 | 245 |  | 1.3 | 18.6 | 7.2 | 21 | 5 | 1.3 | 5.7 |
| 4/11/12 | 9.270 | 18.1 | 7.5 | 160 | 232 |  | 1.2 | 18.7 | 7.2 | 26 | 7 |  | 5.9 |
| 4/12/12 | 9.189 | 18.0 | 7.5 | 140 | 226 | 28.9 | 1.1 | 19.1 | 7.3 | 132 | 8 | 0.2 | 5.6 |
| 4/13/12 | 10.168 | 20.0 | 7.8 |  |  |  | 1.0 | 20.8 | 7.2 |  |  |  | 5.7 |
| 4/14/12 | 9.935 | 19.7 | 7.4 |  |  |  | 1.2 | 20.7 | 7.1 |  |  |  | 5.8 |
| 4/15/12 | 11.353 | 19.0 | 7.4 | 184 | 227 | 23.5 | 1.1 | 20.3 | 7.0 | 37 | 7 | 0.2 | 6.3 |
| 4/16/12 | 9.781 | 20.1 | 7.6 | 140 | 187 |  | 1.0 | 20.4 | 7.2 | 64 | 6 |  | 6.0 |
| 4/17/12 | 9.375 | 20.1 | 7.6 | 148 | 185 |  | 1.3 | 20.7 | 7.2 | 33 | 5 | 0.4 | 5.9 |
| 4/18/12 | 9.541 | 20.3 | 7.5 | 144 | 195 |  | 1.2 | 21.5 | 7.3 | 61 | 6 |  | 5.8 |
| 4/19/12 | 9.447 | 20.2 | 7.6 | 160 | 186 | 23.9 | 1.4 | 20.8 | 7.3 | 22 | 3 | 1.0 | 5.9 |
| 4/20/12 | 10.953 | 19.9 | 7.5 |  |  |  | 1.3 | 20.2 | 7.2 |  |  |  | 5.6 |
| 4/21/12 | 9.628 | 19.9 | 7.5 |  |  |  | 1.3 | 20.6 | 7.2 |  |  |  | 5.3 |
| 4/22/12 | 9.532 | 20.4 | 7.5 | 136 | 202 | 28.0 | 1.2 | 20.6 | 7.3 | 40 | 6 | 0.2 | 5.7 |
| 4/23/12 | 9.227 | 20.5 | 7.4 | 140 | 207 |  | 1.2 | 21.0 | 7.3 | 49 | 5 |  | 6.0 |
| 4/24/12 | 9.297 | 20.6 | 7.5 | 152 | 216 |  | 1.3 | 21.2 | 7.2 | 20 | 5 | 0.9 | 5.9 |
| 4/25/12 | 9.454 | 20.9 | 7.5 | 148 | 216 |  | 1.2 | 21.9 | 7.2 | 41 | 5 |  | 5.5 |
| 4/26/12 | 9.370 | 21.1 | 7.4 | 148 | 203 | 24.5 | 1.3 | 22.0 | 7.1 | 74 | 6 | 0.5 | 5.5 |
| 4/27/12 | 9.436 | 21.0 | 7.4 |  |  |  | 1.3 | 22.5 | 7.0 |  |  |  | 5.6 |
| 4/28/12 | 9.432 | 20.6 | 7.4 |  |  |  | 1.5 | 22.2 | 7.3 |  |  |  | 5.8 |
| 4/29/12 | 9.601 | 21.2 | 7.3 | 144 | 224 | 25.2 | 1.3 | 22.6 | 7.1 | 43 | 5 | 1.1 | 6.0 |
| 4/30/12 | 9.586 | 21.3 | 7.4 | 172 | 245 |  | 0.9 | 22.1 | 7.1 | 21 | 4 |  | 5.8 |
| 5/1/12 | 9.977 | 21.3 | 7.4 | 168 | 213 |  | 1.1 | 22.9 | 7.1 | 112 | 11 | 0.1 | 5.6 |
| 5/2/12 | 9.713 | 21.2 | 7.5 | 172 | 210 |  | 1.0 | 22.4 | 7.1 | 56 | 8 |  | 5.6 |
| 5/3/12 | 9.500 | 21.8 | 7.4 | 144 | 224 | 27.4 | 1.3 | 23.2 | 7.1 | 79 | 10 | 1.5 | 5.5 |
| 5/4/12 | 9.414 | 21.8 | 7.3 |  |  |  | 0.9 | 22.6 | 7.1 |  |  |  | 5.5 |
| 5/5/12 | 9.554 | 21.7 | 7.3 |  |  |  | 1.2 | 23.7 | 7.2 |  |  |  | 5.6 |
| 5/6/12 | 9.573 | 22.1 | 7.3 | 176 | 236 | 26.8 | 1.0 | 24.0 | 7.1 | 118 | 10 | 1.5 | 5.3 |
| 5/7/12 | 9.173 | 21.6 | 7.3 | 140 | 223 |  | 1.2 | 22.3 | 7.0 | 79 | 10 |  | 5.6 |
| 5/8/12 | 8.945 | 21.5 | 7.3 | 140 | 221 |  | 1.1 | 22.3 | 7.1 | 34 | 7 | 1.5 | 5.5 |
| 5/9/12 | 8.892 | 21.8 | 7.3 | 148 | 210 |  | 1.1 | 22.6 | 7.2 | 81 | 10 |  | 5.3 |
| 5/10/12 | 8.758 | 22.3 | 7.1 | 580 | 217 | 21.3 | 1.3 | 22.7 | 6.6 | 155 | 9 | 0.5 | 5.0 |
| 5/11/12 | 9.774 | 21.1 | 7.4 |  |  |  | 1.1 | 21.7 | 7.2 |  |  |  | 5.6 |
| 5/12/12 | 9.782 | 21.5 | 7.3 |  |  |  | 1.2 | 22.1 | 7.2 |  |  |  | 5.7 |
| 5/13/12 | 9.014 | 22.0 | 7.1 | 148 | 216 | 23.3 | 1.0 | 22.9 | 7.0 | 40 | 5 | 0.9 | 5.5 |
| 5/14/12 | 8.727 | 21.6 | 7.2 | 132 | 221 |  | 1.1 | 22.6 | 7.1 | 27 | 6 |  | 5.5 |
| 5/15/12 | 8.466 | 21.9 | 7.2 | 148 | 219 |  | 1.1 | 23.0 | 7.1 | 18 | 6 | 0.6 | 5.4 |
| 5/16/12 | 9.033 | 22.1 | 7.3 | 188 | 214 |  | 1.1 | 23.2 | 7.1 | 20 | 5 |  | 5.5 |
| 5/17/12 | 9.326 | 22.2 | 7.3 | 128 | 207 | 25.2 | 1.0 | 23.1 | 7.0 | 25 | 6 | 0.7 | 5.4 |
| 5/18/12 | 9.132 | 22.0 | 7.2 |  |  |  | 1.1 | 23.2 | 7.0 |  |  |  | 5.7 |
| 5/19/12 | 8.989 | 22.3 | 7.0 |  |  |  | 1.1 | 23.7 | 7.0 |  |  |  | 5.8 |
| 5/20/12 | 9.539 | 21.5 | 7.1 | 180 | 225 | 31.4 | 1.1 | 22.0 | 7.1 | 10 | 7 | 0.5 | 5.8 |
| 5/21/12 | 9.238 | 22.3 | 7.1 | 156 | 235 |  | 0.8 | 22.9 | 7.0 | 7 | 5 |  | 6.0 |
| 5/22/12 | 9.093 | 22.6 | 7.2 | 152 | 219 |  | 1.1 | 23.3 | 7.1 | 7 | 4 | 1.4 | 5.8 |
| 5/23/12 | 9.198 | 22.3 | 7.2 | 116 | 203 |  | 0.8 | 23.7 | 7.0 | 32 | 9 |  | 5.7 |
| 5/24/12 | 9.326 | 22.2 | 7.3 | 152 | 222 | 33.5 | 1.2 | 23.8 | 6.9 | 44 | 6 | 4.1 | 5.3 |
| 5/25/12 | 9.488 | 22.7 | 7.2 |  |  |  | 1.2 | 24.5 | 6.9 |  |  |  | 5.5 |
| 5/26/12 | 8.891 | 22.5 | 7.1 |  |  |  | 1.1 | 23.7 | 6.9 |  |  |  | 5.8 |
| 5/27/12 | 8.365 | 22.9 | 7.1 | 196 | 231 | 29.7 | 1.0 | 25.1 | 6.9 | 20 | 5 | 2.8 | 5.7 |
| 5/28/12 | 8.598 | 22.1 | 7.2 | 152 | 230 |  | 1.3 | 24.5 | 7.0 | 12 | 4 |  | 5.9 |
| 5/29/12 | 8.993 | 22.9 | 7.3 | 272 | 253 |  | 0.9 | 24.4 | 7.1 | 10 | 5 | 4.2 | 5.4 |
| 5/30/12 | 11.202 | 22.6 | 7.4 | 124 | 194 |  | 1.2 | 23.9 | 7.0 | 12 | 6 |  | 5.4 |
| 5/31/12 | 8.785 | 22.4 | 7.3 | 140 | 223 | 29.1 | 1.0 | 23.6 | 7.0 | 13 | 7 | 2.6 | 5.7 |
| 6/1/12 | 8.485 | 22.6 | 7.3 |  |  |  | 1.4 | 23.4 | 7.0 |  |  |  | 5.5 |
| 6/2/12 | 9.087 | 22.7 | 7.3 |  |  |  | 1.1 | 23.6 | 7.1 |  |  |  | 5.8 |
| 6/3/12 | 9.186 | 23.4 | 7.1 | 140 | 196 | 25.4 | 1.0 | 25.0 | 7.0 | 6 | 4 | 7.2 | 5.7 |
| 6/4/12 | 8.739 | 23.2 | 7.3 | 124 | 189 |  | 1.4 | 24.6 | 7.0 | 6 | 4 |  | 5.7 |
| 6/5/12 | 8.448 | 23.8 | 7.1 | 108 | 202 |  | 1.2 | 25.1 | 6.8 | 4 | 5 | 2.7 | 5.6 |
| 6/6/12 | 9.259 | 22.9 | 7.2 | 176 | 236 |  | 1.2 | 24.3 | 7.0 | 6 | 6 |  | 5.7 |
| 6/7/12 | 10.750 | 22.2 | 7.1 | 200 | 251 | 26.0 | 1.4 | 23.8 | 7.1 | 7 | 5 | 2.5 | 5.8 |
| 6/8/12 | 8.985 | 23.3 | 7.2 |  |  |  | 1.0 | 24.5 | 7.1 |  |  |  | 5.7 |
| 6/9/12 | 8.980 | 23.3 | 7.2 |  |  |  | 1.1 | 25.3 | 7.1 |  |  |  | 5.9 |
| 6/10/12 | 8.922 | 23.5 | 7.1 | 140 | 201 | 25.2 | 1.2 | 26.2 | 7.0 | 4 | 2 | 2.0 | 5.7 |
| 6/11/12 | 9.621 | 23.4 | 7.0 | 184 | 157 |  | 1.1 | 25.1 | 7.0 | 3 | 3 |  | 5.7 |
| 6/12/12 | 9.683 | 23.3 | 7.2 | 128 | 217 |  | 1.8 | 24.8 | 6.9 | 6 | 4 | 4.6 | 5.8 |
| 6/13/12 | 9.444 | 23.2 | 7.1 | 159 | 217 |  | 1.9 | 24.6 | 7.0 | 5 | 4 |  | 5.8 |
| 6/14/12 | 9.139 | 23.5 | 7.1 | 176 | 231 | 23.4 | 1.6 | 25.2 | 6.9 | 6 | 6 | 1.9 | 5.8 |
| 6/15/12 | 9.088 | 23.6 | 7.2 |  |  |  | 1.5 | 25.5 | 7.0 |  |  |  | 5.7 |
| 6/16/12 | 9.010 | 23.8 | 7.1 |  |  |  | 1.9 | 25.9 | 7.0 |  |  |  | 5.9 |
| 6/17/12 | 8.890 | 24.2 | 7.1 | 132 | 236 | 23.9 | 1.8 | 26.5 | 7.0 | 4 | 3 | 2.9 | 5.9 |
| 6/18/12 | 8.912 | 23.5 | 7.1 | 176 | 259 |  | 1.5 | 25.5 | 6.9 | 4 | 3 |  | 5.7 |
| 6/19/12 | 9.061 | 23.6 | 7.1 | 176 | 238 |  | 1.9 | 25.4 | 6.9 | 5 | 4 | 3.9 | 5.7 |
| 6/20/12 | 9.124 | 24.0 | 7.1 | 164 | 243 |  | 1.4 | 25.4 | 6.9 | 8 | 5 |  | 5.6 |
| 6/21/12 | 8.947 | 23.7 | 7.2 | 148 | 232 | 33.2 | 1.2 | 25.1 | 6.9 | 11 | 5 | 1.6 | 5.5 |
| 6/22/12 | 8.852 | 23.6 | 7.2 |  |  |  | 1.0 | 25.4 | 7.0 |  |  |  | 5.4 |
| 6/23/12 | 8.869 | 24.3 | 7.2 |  |  |  | 1.1 | 26.7 | 7.1 |  |  |  | 5.4 |
| 6/24/12 | 8.627 | 25.0 | 7.1 | 132 | 252 | 34.1 | 1.0 | 25.6 | 7.1 | 7 | 8 | 16.3 | 5.6 |
| 6/25/12 | 8.496 | 24.7 | 7.1 | 124 | 227 |  | 1.2 | 26.5 | 6.8 | 7 | 5 |  | 5.1 |
| 6/26/12 | 8.822 | 24.6 | 7.2 | 132 | 272 |  | 1.0 | 26.6 | 6.9 | 5 | 3 | 2.7 | 5.2 |
| 6/27/12 | 9.106 | 25.0 | 7.1 | 144 | 225 |  | 1.0 | 26.8 | 7.0 | 5 | 4 |  | 5.7 |
| 6/28/12 | 8.941 | 25.1 | 7.1 | 152 | 253 | 29.0 | 1.0 | 26.6 | 7.0 | 5 | 4 | 2.0 | 5.6 |
| 6/29/12 | 9.076 | 25.5 | 7.0 |  |  |  | 1.0 | 26.7 | 7.0 |  |  |  | 5.6 |
| 6/30/12 | 8.697 | 24.8 | 7.1 |  |  |  | 1.1 | 26.6 | 7.0 |  |  |  | 5.3 |
| 7/1/12 | 8.680 | 25.1 | 7.1 | 132 | 208 | 21.5 | 1.0 | 27.3 | 7.1 | 4 | 3 | 0.9 | 5.4 |
| 7/2/12 | 8.652 | 24.7 | 7.1 | 124 | 195 |  | 1.2 | 27.0 | 7.0 | 6 | 4 |  | 5.7 |
| 7/3/12 | 8.887 | 25.2 | 7.2 | 128 | 186 |  | 0.9 | 26.4 | 7.1 | 6 | 4 | 1.4 | 5.6 |
| 7/4/12 | 8.567 | 25.2 | 7.1 | 108 | 196 |  | 1.2 | 27.2 | 7.0 | 5 | 4 |  | 5.4 |
| 7/5/12 | 8.604 | 24.8 | 7.2 | 108 | 217 | 34.2 | 1.1 | 26.8 | 7.1 | 4 | 4 | 0.4 | 5.5 |
| 7/6/12 | 8.747 | 25.2 | 7.2 |  |  |  | 0.9 | 26.9 | 7.2 |  |  |  | 5.7 |
| 7/7/12 | 8.667 | 25.3 | 7.3 |  |  |  | 1.2 | 27.0 | 7.2 |  |  |  | 5.5 |
| 7/8/12 | 8.589 | 25.0 | 7.1 | 140 | 252 | 26.3 | 1.0 | 26.5 | 7.1 | 5 | 4 | 0.7 | 5.3 |
| 7/9/12 | 8.625 | 25.0 | 7.2 | 160 | 229 |  | 0.9 | 26.9 | 7.3 | 5 | 4 |  | 5.6 |
| 7/10/12 | 8.973 | 25.3 | 7.2 | 180 | 280 |  | 1.2 | 26.8 | 7.2 | 5 | 4 | 0.3 | 5.4 |
| 7/11/12 | 8.834 | 25.6 | 7.3 | 148 | 212 |  | 0.8 | 26.7 | 7.2 | 6 | 5 |  | 5.5 |
| 7/12/12 | 8.500 | 25.8 | 7.3 | 132 | 230 | 37.1 | 1.0 | 27.0 | 7.2 | 5 | 4 | 0.5 | 5.3 |
| 7/13/12 | 8.616 | 25.4 | 7.3 |  |  |  | 1.0 | 27.1 | 7.2 |  |  |  | 5.3 |
| 7/14/12 | 8.840 | 25.7 | 7.2 |  |  |  | 1.2 | 27.6 | 7.1 |  |  |  | 5.5 |
| 7/15/12 | 8.412 | 25.9 | 7.1 | 152 | 242 | 27.5 | 1.1 | 27.6 | 7.1 | 4 | 4 | 0.8 | 5.4 |
| 7/16/12 | 8.685 | 25.8 | 6.6 | 168 | 225 |  | 0.7 | 27.1 | 7.2 | 5 | 4 |  | 5.2 |
| 7/17/12 | 8.772 | 25.7 | 7.3 | 136 | 305 |  | 1.2 | 27.2 | 7.1 | 5 | 6 | 2.0 | 5.6 |
| 7/18/12 | 8.763 | 25.9 | 7.2 | 140 | 214 |  | 1.1 | 27.2 | 7.1 | 6 | 6 |  | 5.5 |
| 7/19/12 | 8.479 | 25.8 | 7.2 | 172 | 216 | 25.1 | 1.0 | 27.5 | 7.1 | 7 | 7 | 1.1 | 5.7 |
| 7/20/12 | 8.453 | 26.3 | 7.3 |  |  |  | 0.9 | 27.6 | 7.1 |  |  |  | 5.7 |
| 7/21/12 | 8.491 | 26.3 | 7.2 |  |  |  | 1.1 | 28.1 | 7.1 |  |  |  | 5.1 |
| 7/22/12 | 8.533 | 26.5 | 7.1 | 132 | 243 | 29.9 | 1.0 | 28.6 | 7.0 | 6 | 4 | 0.6 | 5.2 |
| 7/23/12 | 8.756 | 26.3 | 7.2 | 148 | 212 |  | 0.9 | 27.6 | 7.1 | 4 | 4 |  | 6.0 |
| 7/24/12 | 8.911 | 26.0 | 7.3 | 120 | 203 |  | 1.1 | 27.5 | 7.1 | 5 | 4 | 1.0 | 5.4 |
| 7/25/12 | 8.708 | 26.1 | 7.2 | 128 | 218 |  | 0.9 | 27.7 | 7.1 | 7 | 5 |  | 5.5 |
| 7/26/12 | 8.636 | 26.0 | 7.2 | 136 | 190 | 37.0 | 0.8 | 27.5 | 7.1 | 8 | 3 | 0.3 | 5.3 |
| 7/27/12 | 8.574 | 26.2 | 7.1 |  |  |  | 1.1 | 27.7 | 7.1 |  |  |  | 5.5 |
| 7/28/12 | 8.538 | 26.7 | 7.2 |  |  |  | 1.0 | 28.5 | 7.1 |  |  |  | 5.5 |
| 7/29/12 | 8.259 | 27.1 | 7.1 | 146 | 203 | 28.8 | 1.0 | 28.8 | 7.1 | 3 | 3 | 0.3 | 5.3 |
| 7/30/12 | 8.404 | 26.6 | 7.3 | 151 | 208 |  | 1.1 | 27.7 | 7.1 | 6 | 4 |  | 5.5 |
| 7/31/12 | 8.565 | 26.4 | 7.2 | 140 | 205 |  | 1.1 | 28.3 | 7.2 | 8 | 4 | 0.9 | 5.4 |
| 8/1/12 | 8.296 | 26.7 | 7.2 | 132 | 191 |  | 1.0 | 28.7 | 7.1 | 6 | 4 |  | 5.3 |
| 8/2/12 | 8.430 | 26.5 | 7.2 | 204 | 219 | 30.4 | 1.1 | 28.3 | 7.0 | 5 | 3 | 0.2 | 5.4 |
| 8/3/12 | 8.217 | 26.5 | 7.2 |  |  |  | 1.0 | 28.1 | 7.1 |  |  |  | 5.1 |
| 8/4/12 | 8.664 | 26.8 | 7.2 |  |  |  | 1.1 | 28.6 | 7.2 |  |  |  | 5.2 |
| 8/5/12 | 8.472 | 27.2 | 7.1 | 124 | 210 | 38.9 | 0.9 | 28.5 | 7.1 | 6 | 4 | 0.3 | 5.0 |
| 8/6/12 | 8.293 | 26.8 | 7.2 | 144 | 225 |  | 0.9 | 28.1 | 7.2 | 5 | 5 |  | 5.2 |
| 8/7/12 | 8.646 | 26.6 | 7.2 | 160 | 207 |  | 1.1 | 28.2 | 7.1 | 5 | 5 | 0.2 | 5.1 |
| 8/8/12 | 8.371 | 26.6 | 7.3 | 172 | 219 |  | 0.9 | 28.4 | 7.2 | 4 | 2 |  | 5.3 |
| 8/9/12 | 8.638 | 27.2 | 7.1 | 132 | 191 | 25.9 | 1.0 | 28.5 | 7.0 | 2 | 2 | 0.1 | 5.5 |
| 8/10/12 | 8.227 | 26.9 | 7.2 |  |  |  | 1.0 | 28.3 | 7.1 |  |  |  | 5.5 |
| 8/11/12 | 8.467 | 27.0 | 7.2 |  |  |  | 0.9 | 27.7 | 7.2 |  |  |  | 5.5 |
| 8/12/12 | 8.489 | 27.2 | 7.1 | 180 | 226 | 22.7 | 0.8 | 28.5 | 7.0 | 7 | 7 | 2.0 | 5.0 |
| 8/13/12 | 8.304 | 26.7 | 7.2 | 148 | 255 |  | 1.1 | 27.9 | 7.1 | 4 | 3 |  | 5.5 |
| 8/14/12 | 8.599 | 26.5 | 7.2 | 172 | 198 |  | 1.0 | 27.7 | 7.1 | 3 | 2 | 0.4 | 5.5 |
| 8/15/12 | 8.806 | 26.6 | 7.2 | 136 | 218 |  | 1.1 | 27.7 | 7.1 | 3 | 2 |  | 5.4 |
| 8/16/12 | 9.322 | 26.3 | 7.3 | 168 | 162 | 28.7 | 1.0 | 27.3 | 7.0 | 2 | 2 | 0.1 | 5.4 |
| 8/17/12 | 8.657 | 26.5 | 7.3 |  |  |  | 0.9 | 27.5 | 7.0 |  |  |  | 5.6 |
| 8/18/12 | 10.740 | 26.7 | 7.3 |  |  |  | 0.9 | 27.5 | 7.1 |  |  |  | 5.6 |
| 8/19/12 | 9.457 | 27.0 | 7.2 | 172 | 236 | 22.3 | 0.8 | 27.5 | 7.0 | 2 | 2 | 0.2 | 5.0 |
| 8/20/12 | 8.867 | 26.8 | 7.3 | 148 | 227 |  | 1.2 | 27.4 | 7.0 | 3 | 3 |  | 5.6 |
| 8/21/12 | 9.114 | 26.6 | 7.1 | 136 | 211 |  | 0.9 | 27.8 | 6.9 | 4 | 3 | 0.1 | 5.5 |
| 8/22/12 | 8.979 | 26.7 | 7.2 | 148 | 230 |  | 1.1 | 27.8 | 7.0 | 4 | 4 |  | 5.6 |
| 8/23/12 | 8.481 | 26.6 | 7.1 | 160 | 227 | 25.7 | 1.1 | 27.4 | 6.9 | 6 | 3 | 1.5 | 5.6 |
| 8/24/12 | 8.763 | 26.8 | 7.1 |  |  |  | 1.0 | 27.5 | 7.0 |  |  |  | 5.4 |
| 8/25/12 | 9.263 | 26.7 | 7.2 |  |  |  | 1.0 | 28.1 | 7.0 |  |  |  | 5.5 |
| 8/26/12 | 12.063 | 26.2 | 7.2 | 152 | 176 | 24.0 | 1.3 | 27.2 | 7.0 | 8 | 4 | 2.2 | 5.4 |
| 8/27/12 | 9.271 | 26.7 | 7.2 | 160 | 202 |  | 1.2 | 27.7 | 7.0 | 8 | 4 |  | 5.4 |
| 8/28/12 | 9.241 | 26.0 | 7.2 | 140 | 146 |  | 1.5 | 27.8 | 6.9 | 6 | 2 | 0.7 | 5.3 |
| 8/29/12 | 8.604 | 26.4 | 7.2 | 133 | 291 |  | 1.2 | 27.6 | 7.0 | 6 | 4 |  | 5.6 |
| 8/30/12 | 8.806 | 26.9 | 7.3 | 118 | 203 | 31.1 | 0.9 | 27.7 | 7.0 | 4 | 3 | 0.2 | 5.5 |
| 8/31/12 | 8.673 | 26.5 | 7.2 |  |  |  | 1.0 | 28.0 | 7.2 |  |  |  | 5.6 |
| 9/1/12 | 8.553 | 26.8 | 7.0 |  |  |  | 1.3 | 28.7 | 6.9 |  |  |  | 5.8 |
| 9/2/12 | 8.328 | 26.2 | 7.1 | 125 | 186 | 28.6 | 1.6 | 29.0 | 7.0 | 3 | 2 | 0.3 | 5.9 |
| 9/3/12 | 9.176 | 27.1 | 6.9 | 136 | 218 |  | 1.3 | 28.7 | 6.9 | 3 | 2 |  | 5.4 |
| 9/4/12 | 8.763 | 26.6 | 7.2 | 160 | 213 |  | 1.2 | 28.3 | 7.0 | 4 | 2 | 0.2 | 5.5 |
| 9/5/12 | 8.566 | 27.1 | 7.2 | 148 | 215 |  | 1.1 | 28.4 | 7.0 | 3 | 2 |  | 5.9 |
| 9/6/12 | 8.798 | 27.1 | 7.2 | 140 | 189 | 30.4 | 1.2 | 28.3 | 6.9 | 3 | 2 | 0.3 | 5.7 |
| 9/7/12 | 8.321 | 27.0 | 7.2 |  |  |  | 0.6 | 28.4 | 6.6 |  |  |  | 5.6 |
| 9/8/12 | 9.530 | 26.0 | 6.9 |  |  |  | 1.2 | 27.0 | 6.9 |  |  |  | 5.7 |
| 9/9/12 | 8.795 | 25.5 | 7.1 | 176 | 241 | 24.8 | 1.2 | 27.4 | 6.8 | 4 | 2 | 0.2 | 6.3 |
| 9/10/12 | 8.460 | 26.7 | 7.2 | 148 | 219 |  | 0.5 | 27.3 | 7.0 | 3 | 2 |  | 5.7 |
| 9/11/12 | 8.715 | 26.6 | 7.2 | 156 | 190 |  | 0.8 | 27.2 | 7.0 | 4 | 2 | 0.0 | 5.8 |
| 9/12/12 | 8.623 | 26.8 | 7.3 | 160 | 217 |  | 0.5 | 27.2 | 7.0 | 2 | 2 |  | 6.0 |
| 9/13/12 | 8.785 | 26.1 | 7.3 | 152 | 254 | 34.6 | 1.2 | 26.3 | 7.1 | 2 | 2 | 0.2 | 6.1 |
| 9/14/12 | 8.481 | 25.8 | 7.2 |  |  |  | 1.1 | 25.2 | 7.0 |  |  |  | 5.6 |
| 9/15/12 | 8.744 | 25.5 | 7.0 |  |  |  | 1.1 | 25.6 | 6.9 |  |  |  | 5.6 |
| 9/16/12 | 8.873 | 25.6 | 7.0 | 132 | 238 | 32.7 | 1.2 | 26.0 | 6.8 | 2 | 2 | 0.1 | 5.2 |
| 9/17/12 | 8.605 | 26.2 | 7.2 | 128 | 272 |  | 1.3 | 26.5 | 7.0 | 2 | 2 |  | 5.6 |
| 9/18/12 | 8.620 | 25.7 | 7.3 | 148 | 184 |  | 1.3 | 26.1 | 7.0 | 2 | 2 | 0.6 | 5.9 |
| 9/19/12 | 8.432 | 25.5 | 7.2 | 144 | 230 |  | 1.2 | 26.2 | 7.0 | 2 | 2 |  | 5.7 |
| 9/20/12 | 8.688 | 25.8 | 7.3 | 160 | 218 | 37.2 | 1.3 | 26.3 | 7.1 | 2 | 2 | 0.2 | 5.8 |
| 9/21/12 | 8.504 | 25.7 | 7.2 |  |  |  | 1.4 | 26.6 | 7.0 |  |  |  | 5.8 |
| 9/22/12 | 9.011 | 25.7 | 7.3 |  |  |  | 1.3 | 27.0 | 7.0 |  |  |  | 5.7 |
| 9/23/12 | 8.680 | 25.8 | 7.0 | 176 | 232 | 33.8 | 1.3 | 26.5 | 6.7 | 3 | 2 | 0.0 | 5.4 |
| 9/24/12 | 8.652 | 25.6 | 7.2 | 120 | 239 |  | 1.1 | 26.6 | 7.0 | 4 | 2 |  | 5.5 |
| 9/25/12 | 8.706 | 25.8 | 7.2 | 140 | 224 |  | 1.2 | 26.4 | 7.0 | 7 | 4 | 0.6 | 5.5 |
| 9/26/12 | 8.942 | 25.7 | 7.2 | 192 | 258 |  | 1.0 | 26.7 | 7.0 | 9 | 5 |  | 5.3 |
| 9/27/12 | 11.251 | 25.0 | 7.3 | 140 | 292 | 29.6 | 1.4 | 25.4 | 6.8 | 12 | 2 | 0.7 | 5.6 |
| 9/28/12 | 8.970 | 25.6 | 7.4 |  |  |  | 1.1 | 26.4 | 7.1 |  |  |  | 5.4 |
| 9/29/12 | 10.029 | 24.7 | 7.3 |  |  |  | 1.0 | 25.5 | 7.1 |  |  |  | 5.3 |
| 9/30/12 | 10.818 | 24.1 | 7.3 | 124 | 200 | 32.6 | 1.1 | 25.4 | 7.0 | 10 | 2 | 0.6 | 5.0 |
| 10/1/12 | 8.761 | 25.3 | 7.4 | 132 | 236 |  | 1.0 | 25.6 | 7.2 | 9 | 2 |  | 5.4 |
| 10/2/12 | 8.635 | 25.1 | 7.5 | 128 | 203 |  | 1.2 | 25.0 | 7.1 | 6 | 4 | 0.7 | 5.5 |
| 10/3/12 | 8.940 | 24.9 | 7.5 | 188 | 282 |  | 1.3 | 25.5 | 7.1 | 8 | 6 |  | 5.4 |
| 10/4/12 | 8.808 | 24.8 | 7.5 | 192 | 197 | 32.4 | 1.2 | 25.1 | 7.0 | 8 | 2 | 0.4 | 5.5 |
| 10/5/12 | 8.478 | 24.6 | 7.4 |  |  |  | 1.1 | 23.9 | 7.1 |  |  |  | 5.6 |
| 10/6/12 | 8.554 | 23.8 | 7.5 |  |  |  | 1.6 | 23.0 | 7.2 |  |  |  | 5.6 |
| 10/7/12 | 8.598 | 23.9 | 7.3 | 148 | 247 | 30.5 | 1.3 | 23.2 | 7.0 | 11 | 5 | 0.4 | 5.0 |
| 10/8/12 | 8.504 | 23.7 | 7.4 | 124 | 267 |  | 1.2 | 23.1 | 7.1 | 12 | 7 |  | 5.5 |
| 10/9/12 | 8.788 | 23.9 | 7.5 | 148 | 289 |  | 1.4 | 23.7 | 7.1 | 12 | 7 | 0.4 | 5.4 |
| 10/10/12 | 8.469 | 23.7 | 7.5 | 152 | 239 |  | 1.3 | 23.5 | 7.0 | 9 | 7 |  | 5.6 |
| 10/11/12 | 8.944 | 24.1 | 7.4 | 144 | 266 | 26.2 | 1.3 | 23.9 | 7.0 | 8 | 8 | 0.3 | 5.6 |
| 10/12/12 | 8.301 | 24.2 | 7.3 |  |  |  | 1.3 | 24.6 | 7.1 |  |  |  | 5.6 |
| 10/13/12 | 8.695 | 23.7 | 7.4 |  |  |  | 1.2 | 24.2 | 7.3 |  |  |  | 5.5 |
| 10/14/12 | 8.692 | 24.1 | 7.4 | 144 | 245 | 26.0 | 1.4 | 24.1 | 7.0 | 5 | 3 | 0.2 | 5.6 |
| 10/15/12 | 8.562 | 23.5 | 7.4 | 144 | 237 |  | 1.4 | 24.2 | 7.0 | 4 | 3 |  | 5.8 |
| 10/16/12 | 9.105 | 24.5 | 7.5 | 164 | 304 |  | 1.3 | 24.2 | 7.1 | 6 | 5 | 0.5 | 5.9 |
| 10/17/12 | 8.671 | 23.7 | 7.5 | 196 | 261 |  | 1.5 | 24.2 | 7.1 | 2 | 3 |  | 5.8 |
| 10/18/12 | 8.729 | 23.7 | 7.5 | 172 | 228 | 40.3 | 1.5 | 23.0 | 7.0 | 6 | 3 | 0.2 | 6.0 |
| 10/19/12 | 8.367 | 23.2 | 7.5 |  |  |  | 1.5 | 23.0 | 7.1 |  |  |  | 5.8 |
| 10/20/12 | 8.950 | 23.5 | 7.4 |  |  |  | 1.5 | 23.7 | 7.1 |  |  |  | 5.8 |
| 10/21/12 | 9.277 | 24.2 | 7.3 | 148 | 219 | 30.2 | 1.4 | 25.1 | 7.0 | 5 | 3 | 0.4 | 5.7 |
| 10/22/12 | 8.826 | 23.9 | 7.5 | 164 | 247 |  | 1.3 | 24.3 | 7.3 | 5 | 3 |  | 5.7 |
| 10/23/12 | 9.086 | 24.0 | 7.5 | 184 | 248 |  | 1.3 | 24.2 | 7.3 | 4 | 3 | 0.3 | 5.7 |
| 10/24/12 | 8.718 | 24.0 | 7.4 | 148 | 247 |  | 1.2 | 24.3 | 7.0 | 5 | 3 |  | 5.5 |
| 10/25/12 | 8.760 | 23.6 | 7.5 | 172 | 232 | 28.9 | 1.1 | 23.1 | 7.3 | 4 | 3 | 0.4 | 5.7 |
| 10/26/12 | 8.233 | 23.0 | 7.5 |  |  |  | 1.2 | 21.4 | 7.2 |  |  |  | 5.9 |
| 10/27/12 | 8.990 | 22.8 | 7.4 |  |  |  | 1.3 | 21.5 | 7.1 |  |  |  | 5.6 |
| 10/28/12 | 8.813 | 23.0 | 7.4 | 144 | 217 | 32.7 | 1.3 | 22.8 | 7.0 | 4 | 2 | 1.1 | 5.5 |
| 10/29/12 | 8.352 | 22.7 | 7.4 | 184 | 232 |  | 1.1 | 22.3 | 7.1 | 4 | 2 |  | 5.8 |
| 10/30/12 | 8.602 | 23.0 | 7.4 | 168 | 291 |  | 1.3 | 22.6 | 7.0 | 3 | 2 | 0.2 | 5.8 |
| 10/31/12 | 7.953 | 23.1 | 7.5 | 136 | 250 |  | 1.2 | 22.8 | 7.3 | 3 | 3 |  | 6.0 |
| 11/1/12 | 8.356 | 23.1 | 7.5 | 148 | 220 | 35.5 | 1.6 | 23.0 | 7.3 | 5 | 3 | 0.2 | 6.0 |
| 11/2/12 | 8.184 | 23.3 | 7.5 |  |  |  | 2.0 | 23.5 | 7.3 |  |  |  | 6.5 |
| 11/3/12 | 8.435 | 23.4 | 7.5 |  |  |  | 1.5 | 22.5 | 7.1 |  |  |  | 6.1 |
| 11/4/12 | 8.430 | 23.2 | 7.3 | 164 | 241 | 29.5 | 2.3 | 22.9 | 7.0 | 4 | 3 | 0.1 | 7.0 |
| 11/5/12 | 8.322 | 23.0 | 7.5 | 152 | 242 |  | 1.8 | 22.4 | 7.3 | 4 | 4 |  | 6.5 |
| 11/6/12 | 8.329 | 23.0 | 7.5 | 140 | 249 |  | 1.8 | 22.6 | 7.3 | 4 | 4 | 0.4 | 6.6 |
| 11/7/12 | 8.196 | 22.5 | 7.5 | 144 | 205 |  | 2.3 | 22.7 | 7.0 | 5 | 3 |  | 7.0 |
| 11/8/12 | 8.172 | 22.8 | 7.5 | 136 | 202 | 33.8 | 1.4 | 22.4 | 7.2 | 6 | 4 | 0.3 | 5.2 |
| 11/9/12 | 8.465 | 22.8 | 7.4 |  |  |  | 1.3 | 23.2 | 7.3 |  |  |  | 5.8 |
| 11/10/12 | 8.924 | 22.8 | 7.5 |  |  |  | 1.2 | 23.0 | 7.3 |  |  |  | 5.6 |
| 11/11/12 | 10.523 | 21.1 | 7.3 | 148 | 220 | 27.9 | 1.3 | 21.5 | 7.0 | 11 | 4 | 0.3 | 5.0 |
| 11/12/12 | 8.750 | 21.5 | 7.6 | 128 | 222 |  | 1.3 | 21.0 | 7.1 | 10 | 4 |  | 6.0 |
| 11/13/12 | 8.871 | 21.9 | 7.6 | 280 | 218 |  | 1.3 | 21.8 | 7.3 | 7 | 4 | 1.6 | 5.8 |
| 11/14/12 | 8.400 | 21.8 | 7.6 | 160 | 221 |  | 1.4 | 21.2 | 7.2 | 8 | 5 |  | 6.1 |
| 11/15/12 | 8.598 | 21.9 | 7.5 | 168 | 234 | 33.9 | 1.1 | 21.2 | 7.3 | 6 | 4 | 0.1 | 6.0 |
| 11/16/12 | 8.136 | 21.7 | 7.5 |  |  |  | 1.5 | 21.3 | 7.1 |  |  |  | 6.3 |
| 11/17/12 | 8.488 | 21.2 | 7.3 |  |  |  | 1.3 | 21.0 | 7.0 |  |  |  | 6.3 |
| 11/18/12 | 8.637 | 21.4 | 7.4 | 188 | 265 | 28.6 | 1.5 | 21.2 | 7.0 | 5 | 2 | 0.1 | 5.7 |
| 11/19/12 | 8.272 | 21.8 | 7.5 | 164 | 239 |  | 1.2 | 21.5 | 7.4 | 3 | 3 |  | 6.0 |
| 11/20/12 | 8.298 | 22.0 | 7.5 | 136 | 234 |  | 1.2 | 22.2 | 7.3 | 3 | 2 | 0.3 | 6.0 |
| 11/21/12 | 8.064 | 21.4 | 7.5 | 168 | 262 |  | 1.4 | 21.8 | 7.3 | 3 | 2 |  | 6.2 |
| 11/22/12 | 7.575 | 21.3 | 7.4 | 128 | 234 | 25.8 | 1.2 | 21.6 | 7.3 | 3 | 3 | 0.3 | 6.1 |
| 11/23/12 | 7.232 | 21.0 | 7.4 |  |  |  | 1.4 | 20.5 | 7.2 |  |  |  | 5.5 |
| 11/24/12 | 8.234 | 20.8 | 7.5 |  |  |  | 1.3 | 20.0 | 7.1 |  |  |  | 5.2 |
| 11/25/12 | 8.437 | 21.2 | 7.4 | 172 | 242 | 29.8 | 1.5 | 20.8 | 7.0 | 4 | 3 | 0.5 | 5.9 |
| 11/26/12 | 8.181 | 20.5 | 7.5 | 152 | 265 |  | 1.2 | 19.8 | 7.1 | 3 | 3 |  | 6.4 |
| 11/27/12 | 8.393 | 20.9 | 7.5 | 116 | 229 |  | 1.7 | 19.5 | 7.5 | 4 | 3 | 0.1 | 6.3 |
| 11/28/12 | 8.296 | 20.8 | 7.5 | 140 | 259 |  | 0.8 | 19.9 | 7.3 | 6 | 3 |  | 6.4 |
| 11/29/12 | 8.356 | 22.0 | 7.5 | 240 | 233 | 31.3 | 1.2 | 20.0 | 7.2 | 4 | 3 | 0.1 | 6.2 |
| 11/30/12 | 8.263 | 21.0 | 7.4 |  |  |  | 0.9 | 20.8 | 7.3 |  |  |  | 6.2 |
| 12/1/12 | 8.482 | 20.8 | 7.5 |  |  |  | 0.6 | 21.0 | 7.4 |  |  |  | 6.1 |
| 12/2/12 | 8.298 | 21.2 | 7.3 | 124 | 229 | 30.7 | 0.8 | 21.5 | 7.0 | 4 | 3 | 0.6 | 5.4 |
| 12/3/12 | 8.617 | 20.7 | 7.4 | 140 | 211 |  | 0.5 | 21.2 | 7.1 | 3 | 3 |  | 6.1 |
| 12/4/12 | 8.178 | 21.0 | 7.5 | 152 | 235 |  | 0.4 | 20.7 | 7.1 | 2 | 2 | 0.1 | 6.1 |
| 12/5/12 | 8.253 | 20.9 | 7.4 | 216 | 233 |  | 0.6 | 20.3 | 7.1 | 3 | 2 |  | 6.1 |
| 12/6/12 | 8.278 | 21.0 | 7.6 | 160 | 239 | 31.7 | 0.6 | 20.7 | 7.3 | 3 | 2 | 0.1 | 6.0 |
| 12/7/12 | 8.300 | 20.2 | 7.6 |  |  |  | 0.4 | 20.2 | 7.3 |  |  |  | 6.0 |
| 12/8/12 | 8.491 | 20.2 | 7.5 |  |  |  | 0.8 | 20.2 | 7.1 |  |  |  | 6.0 |
| 12/9/12 | 8.397 | 20.0 | 7.5 | 140 | 206 | 32.3 | 0.5 | 19.9 | 7.1 | 4 | 3 | 0.1 | 5.2 |
| 12/10/12 | 8.595 | 20.0 | 7.5 | 200 | 223 |  | 0.5 | 18.3 | 7.4 | 3 | 3 |  | 6.3 |
| 12/11/12 | 8.474 | 19.9 | 7.6 | 120 | 231 |  | 0.7 | 18.7 | 7.4 | 3 | 2 | 0.1 | 6.2 |
| 12/12/12 | 8.524 | 19.8 | 7.5 | 168 | 239 |  | 0.7 | 18.8 | 7.2 | 3 | 3 |  | 6.1 |
| 12/13/12 | 8.342 | 20.0 | 7.5 | 160 | 254 | 28.1 | 0.4 | 18.9 | 7.1 | 4 | 3 | 0.0 | 6.4 |
| 12/14/12 | 8.345 | 19.9 | 7.4 |  |  |  | 0.4 | 18.9 | 7.1 |  |  |  | 6.1 |
| 12/15/12 | 8.571 | 19.4 | 7.5 |  |  |  | 1.3 | 19.0 | 7.1 |  |  |  | 5.3 |
| 12/16/12 | 7.987 | 20.0 | 7.3 | 136 | 206 | 25.8 | 0.9 | 20.0 | 7.0 | 4 | 3 | 0.1 | 5.6 |
| 12/17/12 | 7.998 | 19.7 | 7.6 | 152 | 219 |  | 0.7 | 19.3 | 7.1 | 4 | 3 |  | 6.1 |
| 12/18/12 | 7.724 | 19.9 | 7.5 | 148 | 204 |  | 1.7 | 19.5 | 7.1 | 4 | 3 | 0.1 | 6.8 |
| 12/19/12 | 7.932 | 19.8 | 7.5 | 124 | 212 |  | 0.8 | 19.6 | 7.2 | 5 | 2 |  | 6.2 |
| 12/20/12 | 7.776 | 19.0 | 7.4 | 116 | 239 | 29.2 | 0.4 | 17.5 | 7.3 | 4 | 2 | 0.5 | 6.6 |
| 12/21/12 | 7.623 | 18.8 | 7.4 |  |  |  | 1.0 | 17.8 | 7.1 |  |  |  | 6.1 |
| 12/22/12 | 7.675 | 18.7 | 7.4 |  |  |  | 1.0 | 18.2 | 7.2 |  |  |  | 6.6 |
| 12/23/12 | 7.258 | 19.0 | 8.5 | 120 | 208 | 30.3 | 0.6 | 18.3 | 7.1 | 4 | 3 | 0.1 | 6.3 |
| 12/24/12 | 7.759 | 17.9 | 7.3 | 144 | 244 |  | 0.9 | 17.3 | 7.1 | 4 | 3 |  | 6.3 |
| 12/25/12 | 7.489 | 17.0 | 7.5 | 156 | 239 |  | 0.4 | 15.8 | 7.2 | 5 | 3 |  | 6.5 |
| 12/26/12 | 7.737 | 17.7 | 7.5 | 148 | 204 |  | 1.0 | 15.3 | 7.2 | 4 | 3 |  | 6.9 |
| 12/27/12 | 8.399 | 17.4 | 7.5 | 140 | 211 | 30.2 | 0.8 | 15.4 | 7.2 | 4 | 3 | 0.4 | 6.7 |
| 12/28/12 | 7.970 | 17.7 | 7.5 |  |  |  | 1.1 | 16.3 | 7.1 |  |  |  | 6.6 |
| 12/29/12 | 7.956 | 17.1 | 7.5 |  |  |  | 1.0 | 16.0 | 7.5 |  |  |  | 6.3 |
| 12/30/12 | 7.853 | 17.5 | 7.4 | 136 | 247 | 28.0 | 0.8 | 16.4 | 7.0 | 5 | 4 | 0.1 | 6.4 |
| 12/31/12 | 9.318 | 16.2 | 7.3 | 148 | 211 |  | 0.8 | 16.0 | 7.1 | 5 | 3 |  | 6.7 |
| 1/1/13 | 8.173 | 18.0 | 7.8 | 172 | 280 |  | 0.8 | 16.0 | 7.0 | 6 | 6 | 0.5 | 5.5 |
| 1/2/13 | 8.193 | 17.3 | 7.5 | 124 | 246 |  | 0.4 | 16.4 | 7.2 | 5 | 2 |  | 6.4 |
| 1/3/13 | 8.037 | 17.3 | 7.6 | 164 | 239 | 29.6 | 0.8 | 16.5 | 7.2 | 5 | 2 | 0.4 | 6.5 |
| 1/4/13 | 7.906 | 16.9 | 7.6 |  |  |  | 0.8 | 16.4 | 7.2 |  |  |  | 6.6 |
| 1/5/13 | 7.888 | 16.0 | 7.4 |  |  |  | 0.4 | 17.0 | 7.3 |  |  |  | 5.7 |
| 1/6/13 | 7.805 | 17.5 | 7.3 | 144 | 182 | 32.8 | 0.7 | 17.4 | 7.1 | 7 | 3 | 0.1 | 5.5 |
| 1/7/13 | 8.153 | 17.2 | 7.6 | 136 | 202 |  | 0.8 | 16.5 | 7.2 | 8 | 4 |  | 6.5 |
| 1/8/13 | 7.920 | 17.2 | 7.5 | 148 | 251 |  | 0.8 | 16.6 | 7.1 | 8 | 4 | 0.2 | 6.5 |
| 1/9/13 | 8.229 | 17.3 | 7.6 | 168 | 238 |  | 0.9 | 17.0 | 7.1 | 10 | 4 |  | 6.3 |
| 1/10/13 | 9.778 | 17.2 | 7.5 | 112 | 211 | 24.2 | 0.4 | 17.8 | 7.3 | 6 | 4 | 0.3 | 6.4 |
| 1/11/13 | 8.588 | 17.0 | 7.5 |  |  |  | 0.6 | 17.0 | 7.3 |  |  |  | 6.0 |
| 1/12/13 | 8.377 | 17.0 | 7.4 |  |  |  | 0.5 | 16.0 | 7.0 |  |  |  | 6.1 |
| 1/13/13 | 8.471 | 17.0 | 7.5 | 148 | 240 | 29.7 | 0.8 | 15.4 | 7.1 | 6 | 4 | 0.2 | 6.3 |
| 1/14/13 | 8.395 | 16.5 | 7.6 | 152 | 227 |  | 0.4 | 15.5 | 6.8 | 7 | 4 |  | 6.6 |
| 1/15/13 | 8.373 | 16.9 | 7.7 | 248 | 237 |  | 0.9 | 15.7 | 7.5 | 7 | 5 | 0.3 | 6.2 |
| 1/16/13 | 8.529 | 17.1 | 7.7 | 136 | 248 |  | 0.7 | 16.0 | 7.2 | 8 | 5 |  | 6.4 |
| 1/17/13 | 8.250 | 17.0 | 7.6 | 160 | 245 | 39.3 | 0.6 | 16.4 | 7.1 | 8 | 4 | 0.1 | 6.4 |
| 1/18/13 | 8.480 | 17.0 | 7.7 |  |  |  | 0.9 | 16.5 | 7.2 |  |  |  | 6.4 |
| 1/19/13 | 8.133 | 16.0 | 7.3 |  |  |  | 1.4 | 17.0 | 7.1 |  |  |  | 5.0 |
| 1/20/13 | 8.007 | 17.5 | 7.5 | 132 | 246 | 32.7 | 0.4 | 17.9 | 7.0 | 8 | 4 | 0.2 | 5.3 |
| 1/21/13 | 8.283 | 16.0 | 7.6 | 164 | 225 |  | 0.5 | 16.0 | 7.0 | 10 | 4 |  | 5.4 |
| 1/22/13 | 8.258 | 17.1 | 7.7 | 204 | 258 |  | 0.8 | 16.4 | 7.0 | 10 | 5 | 0.9 | 6.2 |
| 1/23/13 | 8.254 | 17.5 | 7.6 | 148 | 237 |  | 0.7 | 17.4 | 7.1 | 8 | 5 |  | 6.3 |
| 1/24/13 | 8.196 | 17.1 | 7.7 | 132 | 230 | 36.1 | 0.8 | 16.9 | 7.0 | 6 | 4 | 0.5 | 6.3 |
| 1/25/13 | 8.144 | 16.7 | 7.6 |  |  |  | 0.9 | 16.5 | 7.0 |  |  |  | 6.4 |
| 1/26/13 | 8.354 | 16.0 | 7.5 |  |  |  | 0.5 | 16.0 | 7.1 |  |  |  | 5.4 |
| 1/27/13 | 8.441 | 17.2 | 7.5 | 144 | 232 | 27.3 | 0.7 | 17.7 | 7.0 | 7 | 4 | 0.4 | 5.7 |
| 1/28/13 | 8.558 | 17.9 | 7.5 | 136 | 242 |  | 0.4 | 18.3 | 7.0 | 6 | 3 |  | 6.4 |
| 1/29/13 | 8.917 | 17.8 | 7.6 | 240 | 377 |  | 0.8 | 18.2 | 7.0 | 6 | 7 | 0.6 | 6.1 |
| 1/30/13 | 8.404 | 17.3 | 7.7 | 140 | 256 |  | 0.5 | 16.8 | 7.4 | 6 | 4 |  | 6.4 |
| 1/31/13 | 8.196 | 17.5 | 7.5 | 136 | 256 | 29.2 | 0.4 | 17.2 | 7.1 | 6 | 4 | 0.2 | 6.2 |
| 2/1/13 | 8.192 | 16.9 | 7.5 |  |  |  | 0.7 | 16.3 | 6.9 |  |  |  | 6.5 |
| 2/2/13 | 8.324 | 16.0 | 7.6 |  |  |  | 0.9 | 17.0 | 6.9 |  |  |  | 5.6 |
| 2/3/13 | 8.413 | 17.5 | 7.4 | 148 | 228 | 29.8 | 0.4 | 17.5 | 7.0 | 7 | 5 | 0.3 | 5.3 |
| 2/4/13 | 8.335 | 17.7 | 7.5 | 160 | 237 |  | 0.8 | 17.8 | 6.9 | 6 | 4 |  | 6.2 |
| 2/5/13 | 8.174 | 18.0 | 7.6 | 148 | 259 |  | 0.3 | 17.0 | 6.8 | 8 | 5 | 0.6 | 6.0 |
| 2/6/13 | 8.289 | 17.0 | 7.6 | 168 | 239 |  | 0.8 | 18.0 | 7.1 | 7 | 4 |  | 5.6 |
| 2/7/13 | 8.366 | 17.0 | 7.6 | 184 | 251 | 32.8 | 0.7 | 18.3 | 7.2 | 4 | 4 | 0.2 | 6.1 |
| 2/8/13 | 8.059 | 17.2 | 7.6 |  |  |  | 0.4 | 17.6 | 7.0 |  |  |  | 6.3 |
| 2/9/13 | 8.389 | 17.0 | 7.4 |  |  |  | 0.4 | 16.5 | 7.3 |  |  |  | 5.6 |
| 2/10/13 | 8.370 | 17.5 | 7.5 | 144 | 254 | 24.1 | 1.8 | 17.9 | 6.9 | 5 | 3 | 0.4 | 6.1 |
| 2/11/13 | 8.028 | 17.5 | 7.6 | 168 | 206 |  | 1.3 | 17.0 | 6.8 | 5 | 3 |  | 6.6 |
| 2/12/13 | 10.104 | 16.5 | 7.5 | 236 | 251 |  | 1.5 | 16.8 | 6.7 | 6 | 4 | 0.5 | 5.7 |
| 2/13/13 | 8.910 | 16.8 | 7.7 | 144 | 219 |  | 1.2 | 16.3 | 7.0 | 5 | 4 |  | 6.6 |
| 2/14/13 | 8.330 | 17.7 | 7.7 | 136 | 239 | 28.6 | 0.8 | 17.2 | 6.9 | 4 | 3 | 0.3 | 6.2 |
| 2/15/13 | 8.241 | 17.0 | 7.6 |  |  |  | 1.0 | 16.4 | 7.0 |  |  |  | 6.5 |
| 2/16/13 | 8.351 | 16.0 | 7.6 |  |  |  | 0.9 | 17.0 | 7.2 |  |  |  | 5.6 |
| 2/17/13 | 8.250 | 17.0 | 7.5 | 128 | 238 | 24.9 | 1.2 | 18.0 | 7.3 | 14 | 5 | 0.3 | 6.2 |
| 2/18/13 | 8.472 | 17.3 | 7.6 | 152 | 232 |  | 0.9 | 17.1 | 6.8 | 7 | 3 |  | 6.4 |
| 2/19/13 | 8.277 | 17.1 | 7.5 | 152 | 261 |  | 1.4 | 17.3 | 6.8 | 6 | 6 | 0.3 | 6.1 |
| 2/20/13 | 10.676 | 15.8 | 7.3 | 168 | 203 |  | 1.3 | 16.1 | 6.8 | 4 | 4 |  | 6.2 |
| 2/21/13 | 11.774 | 14.5 | 7.5 | 156 | 193 | 20.7 | 1.3 | 14.7 | 6.6 | 4 | 5 | 0.3 | 6.5 |
| 2/22/13 | 9.166 | 16.0 | 7.6 |  |  |  | 2.3 | 15.0 | 6.9 |  |  |  | 6.4 |
| 2/23/13 | 8.827 | 16.0 | 7.5 |  |  |  | 3.6 | 15.0 | 7.1 |  |  |  | 5.7 |
| 2/24/13 | 8.743 | 16.5 | 7.5 | 124 | 177 | 24.4 | 1.4 | 16.0 | 6.6 | 4 | 4 | 1.0 | 6.5 |
| 2/25/13 | 12.989 | 14.2 | 7.2 | 228 | 171 |  | 1.3 | 16.1 | 6.9 | 6 | 5 |  | 5.2 |
| 2/26/13 | 10.122 | 15.6 | 7.7 | 144 | 155 |  | 1.1 | 14.5 | 6.8 | 4 | 3 | 0.8 | 6.7 |
| 2/27/13 | 9.440 | 16.2 | 7.7 | 140 | 173 |  | 1.3 | 15.4 | 6.8 | 4 | 3 |  | 6.5 |
| 2/28/13 | 8.982 | 16.2 | 7.7 | 172 | 198 | 29.7 | 1.4 | 15.8 | 6.8 | 5 | 3 | 0.3 | 6.4 |
| 3/1/13 | 8.775 | 16.1 | 7.6 |  |  |  | 1.3 | 16.0 | 6.9 |  |  |  | 6.6 |
| 3/2/13 | 8.668 | 15.7 | 7.5 |  |  |  | 1.6 | 15.7 | 6.6 |  |  |  | 6.8 |
| 3/3/13 | 8.799 | 16.0 | 7.6 | 96 | 196 | 29.5 | 1.9 | 17.0 | 7.0 | 5 | 4 | 0.2 | 6.5 |
| 3/4/13 | 8.546 | 16.9 | 7.6 | 140 | 202 |  | 1.3 | 17.1 | 6.9 | 5 | 4 |  | 6.3 |
| 3/5/13 | 8.682 | 16.4 | 7.6 | 120 | 225 |  | 1.4 | 15.9 | 6.9 | 4 | 2 | 0.5 | 6.5 |
| 3/6/13 | 8.606 | 16.3 | 7.6 | 140 | 239 |  | 1.5 | 16.3 | 6.8 | 16 | 24 |  | 6.5 |
| 3/7/13 | 8.556 | 16.4 | 7.6 | 160 | 264 | 34.5 | 1.5 | 16.8 | 6.7 | 3 | 3 | 0.2 | 6.2 |
| 3/8/13 | 8.592 | 16.9 | 7.6 |  |  |  | 1.5 | 17.0 | 7.0 |  |  |  | 6.3 |
| 3/9/13 | 9.207 | 15.5 | 7.5 |  |  |  | 1.4 | 17.0 | 6.7 |  |  |  | 5.7 |
| 3/10/13 | 9.220 | 15.0 | 7.6 | 140 | 267 | 25.5 | 1.6 | 16.0 | 7.4 | 4 | 3 | 0.2 | 5.5 |
| 3/11/13 | 8.673 | 16.4 | 7.7 | 124 | 190 |  | 1.5 | 15.9 | 7.0 | 4 | 3 |  | 6.2 |
| 3/12/13 | 8.865 | 16.8 | 7.6 | 208 | 226 |  | 1.4 | 16.6 | 6.9 | 5 | 3 | 1.7 | 6.3 |
| 3/13/13 | 8.659 | 16.6 | 7.6 | 116 | 197 |  | 1.5 | 17.1 | 6.9 | 4 | 3 |  | 6.6 |
| 3/14/13 | 8.389 | 17.0 | 7.5 | 148 | 190 | 31.6 | 1.6 | 17.7 | 7.0 | 3 | 3 | 0.1 | 6.5 |
| 3/15/13 | 8.424 | 17.5 | 7.4 |  |  |  | 1.3 | 18.3 | 7.0 |  |  |  | 6.5 |
| 3/16/13 | 7.979 | 17.2 | 7.4 |  |  |  | 1.3 | 18.5 | 6.7 |  |  |  | 6.5 |
| 3/17/13 | 7.693 | 16.0 | 7.6 | 136 | 182 | 32.2 | 2.3 | 17.0 | 7.1 | 3 | 2 | 0.2 | 6.5 |
| 3/18/13 | 7.709 | 16.3 | 7.4 | 140 | 226 |  | 1.5 | 16.8 | 6.9 | 4 | 2 |  | 6.4 |
| 3/19/13 | 7.743 | 16.8 | 7.4 | 128 | 207 |  | 1.3 | 17.2 | 7.0 | 11 | 14 | 1.9 | 6.3 |
| 3/20/13 | 7.550 | 16.7 | 7.5 | 104 | 256 |  | 1.5 | 17.0 | 7.0 | 3 | 2 |  | 6.6 |
| 3/21/13 | 7.824 | 16.4 | 7.3 | 156 | 227 | 38.7 | 1.3 | 16.2 | 7.0 | 3 | 2 | 0.2 | 6.5 |
| 3/22/13 | 7.730 | 16.3 | 7.5 |  |  |  | 1.6 | 16.3 | 7.1 |  |  |  | 6.3 |
| 3/23/13 | 7.918 | 16.1 | 7.3 |  |  |  | 1.4 | 16.1 | 6.9 |  |  |  | 5.4 |
| 3/24/13 | 8.217 | 16.0 | 7.5 | 192 | 267 | 36.8 | 1.8 | 15.5 | 7.1 | 4 | 3 | 0.2 | 5.2 |
| 3/25/13 | 8.672 | 16.7 | 7.6 | 124 | 245 |  | 1.4 | 15.9 | 7.0 | 5 | 3 |  | 6.4 |
| 3/26/13 | 8.460 | 16.8 | 7.5 | 168 | 233 |  | 1.3 | 16.5 | 6.9 | 5 | 2 | 0.2 | 6.6 |
| 3/27/13 | 8.567 | 17.0 | 7.6 | 140 | 231 |  | 1.3 | 16.4 | 6.9 | 5 | 3 |  | 6.6 |
| 3/28/13 | 8.294 | 17.2 | 7.5 | 204 | 282 | 30.7 | 1.4 | 17.5 | 6.8 | 5 | 3 | 0.3 | 6.5 |
| 3/29/13 | 8.216 | 17.4 | 7.4 |  |  |  | 1.3 | 17.8 | 6.9 |  |  |  | 6.3 |
| 3/30/13 | 8.220 | 16.1 | 7.2 |  |  |  | 1.6 | 16.9 | 6.8 |  |  |  | 5.7 |
| 3/31/13 | 9.373 | 16.5 | 7.4 | 172 | 209 | 29.1 | 1.5 | 16.3 | 6.7 | 6 | 3 | 0.5 | 5.9 |
| 4/1/13 | 8.630 | 17.8 | 7.5 | 152 | 220 |  | 1.3 | 18.2 | 6.9 | 6 | 2 |  | 6.4 |
| 4/2/13 | 12.731 | 16.2 | 7.5 | 188 | 178 |  | 1.2 | 16.4 | 6.9 | 7 | 4 | 1.3 | 6.3 |
| 4/3/13 | 18.473 | 14.8 | 7.6 | 120 | 172 |  | 1.7 | 14.9 | 6.8 | 8 | 5 |  | 6.7 |
| 4/4/13 | 15.595 | 15.0 | 7.6 | 100 | 173 | 26.2 | 1.5 | 13.9 | 6.8 | 5 | 4 | 0.8 | 7.1 |
| 4/5/13 | 10.770 | 16.4 | 7.7 |  |  |  | 1.5 | 16.3 | 7.0 |  |  |  | 6.7 |
| 4/6/13 | 10.124 | 15.4 | 7.6 |  |  |  | 1.5 | 16.0 | 7.0 |  |  |  | 6.4 |
| 4/7/13 | 9.999 | 16.7 | 7.5 | 156 | 253 | 26.6 | 1.6 | 17.5 | 6.9 | 4 | 3 | 0.7 | 6.4 |
| 4/8/13 | 9.858 | 17.9 | 7.5 | 124 | 243 |  | 1.1 | 18.8 | 7.1 | 4 | 2 |  | 6.1 |
| 4/9/13 | 9.592 | 18.0 | 7.6 | 200 | 188 |  | 1.2 | 19.0 | 7.1 | 6 | 3 | 0.8 | 6.1 |
| 4/10/13 | 15.726 | 13.8 | 7.4 | 156 | 162 |  | 1.8 | 15.7 | 7.0 | 7 | 5 |  | 5.6 |
| 4/11/13 | 11.868 | 16.3 | 7.7 | 100 | 303 | 41.5 | 1.2 | 15.4 | 7.0 | 4 | 3 | 0.4 | 6.7 |
| 4/12/13 | 10.251 | 16.8 | 7.6 |  |  |  | 1.0 | 16.6 | 7.1 |  |  |  | 6.6 |
| 4/13/13 | 9.950 | 15.9 | 7.5 |  |  |  | 1.3 | 15.6 | 6.9 |  |  |  | 6.1 |
| 4/14/13 | 9.870 | 16.2 | 7.5 | 136 | 209 | 22.8 | 1.3 | 16.0 | 6.9 | 3 | 3 | 0.4 | 6.2 |
| 4/15/13 | 9.661 | 17.9 | 7.5 | 108 | 203 |  | 1.2 | 18.8 | 7.1 | 3 | 3 |  | 6.4 |
| 4/16/13 | 9.506 | 17.5 | 7.5 | 152 | 254 |  | 1.0 | 17.9 | 7.0 | 3 | 2 | 1.0 | 6.1 |
| 4/17/13 | 10.715 | 18.2 | 7.4 | 156 | 158 |  | 1.1 | 18.8 | 6.9 | 8 | 6 |  | 6.3 |
| 4/18/13 | 21.197 | 16.1 | 7.7 | 136 | 139 | 24.2 | 2.0 | 15.3 | 6.9 | 5 | 6 | 0.6 | 6.4 |
| 4/19/13 | 11.724 | 17.0 | 7.6 |  |  |  | 1.3 | 16.5 | 7.0 |  |  |  | 6.7 |
| 4/20/13 | 10.487 | 17.0 | 7.6 |  |  |  | 1.5 | 18.1 | 6.9 |  |  |  | 5.9 |
| 4/21/13 | 9.965 | 17.1 | 7.5 | 112 | 158 | 21.7 | 1.3 | 17.7 | 7.0 | 2 | 3 | 0.3 | 6.6 |
| 4/22/13 | 10.290 | 17.9 | 7.5 | 116 | 244 |  | 1.1 | 18.8 | 7.0 | 3 | 3 |  | 6.5 |
| 4/23/13 | 10.022 | 17.1 | 7.6 | 124 | 242 |  | 1.2 | 16.7 | 7.0 | 3 | 2 | 0.5 | 6.4 |
| 4/24/13 | 9.707 | 17.5 | 7.5 | 152 | 223 |  | 1.2 | 17.3 | 7.5 | 3 | 2 |  | 6.7 |
| 4/25/13 | 9.611 | 18.0 | 7.5 | 160 | 227 | 24.3 | 1.1 | 18.2 | 7.0 | 2 | 2 | 0.3 | 6.5 |
| 4/26/13 | 9.818 | 17.6 | 7.4 |  |  |  | 1.1 | 17.8 | 7.0 |  |  |  | 6.4 |
| 4/27/13 | 12.328 | 16.5 | 7.5 |  |  |  | 1.4 | 17.0 | 6.9 |  |  |  | 5.9 |
| 4/28/13 | 10.298 | 16.5 | 7.5 | 132 | 173 | 18.7 | 1.3 | 19.5 | 6.9 | 3 | 3 | 0.5 | 6.3 |
| 4/29/13 | 10.051 | 18.8 | 7.5 | 160 | 184 |  | 1.2 | 19.9 | 7.0 | 4 | 3 |  | 6.3 |
| 4/30/13 | 9.879 | 19.5 | 7.5 | 148 | 176 |  | 1.9 | 20.5 | 7.1 | 4 | 3 | 0.9 | 6.3 |
| 5/1/13 | 9.874 | 19.0 | 7.4 | 164 | 208 |  | 1.0 | 20.6 | 6.9 | 4 | 5 |  | 6.4 |
| 5/2/13 | 8.574 | 17.4 | 7.6 | 132 | 212 | 20.8 | 1.2 | 17.3 | 7.1 | 3 | 6 | 0.7 | 6.2 |
| 5/3/13 | 9.405 | 18.3 | 7.3 |  |  |  | 1.0 | 17.8 | 6.9 |  |  |  | 6.6 |
| 5/4/13 | 9.443 | 16.9 | 7.4 |  |  |  | 1.5 | 17.0 | 7.0 |  |  |  | 6.5 |
| 5/5/13 | 9.395 | 17.0 | 7.5 | 140 | 212 | 24.9 | 1.2 | 17.5 | 7.0 | 3 | 3 | 0.1 | 5.5 |
| 5/6/13 | 9.258 | 18.4 | 7.4 | 116 | 176 |  | 1.0 | 19.3 | 7.0 | 4 | 3 |  | 6.4 |
| 5/7/13 | 9.534 | 19.2 | 7.4 | 132 | 207 |  | 1.1 | 20.1 | 6.9 | 4 | 5 | 1.7 | 6.3 |
| 5/8/13 | 10.349 | 18.0 | 7.4 | 280 | 196 |  | 0.9 | 21.0 | 7.0 | 6 | 6 |  | 6.2 |
| 5/9/13 | 12.995 | 18.8 | 7.6 | 168 | 194 | 19.7 | 1.2 | 19.4 | 6.8 | 5 | 7 | 2.3 | 6.2 |
| 5/10/13 | 10.960 | 19.2 | 7.5 |  |  |  | 1.1 | 19.9 | 6.9 |  |  |  | 6.4 |
| 5/11/13 | 10.166 | 19.6 | 7.4 |  |  |  | 1.2 | 20.5 | 6.9 |  |  |  | 6.8 |
| 5/12/13 | 9.446 | 19.5 | 7.4 | 112 | 203 | 23.1 | 1.1 | 20.6 | 6.9 | 3 | 3 | 1.2 | 6.1 |
| 5/13/13 | 9.703 | 19.3 | 7.3 | 132 | 178 |  | 1.2 | 20.3 | 6.9 | 3 | 3 |  | 6.3 |
| 5/14/13 | 9.522 | 19.3 | 7.4 | 128 | 171 |  | 1.1 | 20.9 | 6.9 | 3 | 3 | 0.9 | 6.3 |
| 5/15/13 | 10.359 | 19.4 | 7.4 | 156 | 157 |  | 0.9 | 20.6 | 6.9 | 3 | 3 |  | 6.2 |
| 5/16/13 | 10.480 | 18.9 | 7.4 | 216 | 216 | 24.6 | 1.2 | 19.8 | 6.9 | 3 | 3 | 0.6 | 6.0 |
| 5/17/13 | 9.795 | 19.3 | 7.4 |  |  |  | 1.1 | 20.0 | 6.9 |  |  |  | 6.1 |
| 5/18/13 | 9.883 | 19.6 | 7.4 |  |  |  | 1.1 | 21.7 | 6.9 |  |  |  | 6.4 |
| 5/19/13 | 12.273 | 19.5 | 7.4 | 264 | 172 | 23.1 | 1.1 | 21.7 | 6.9 | 3 | 3 | 0.7 | 6.2 |
| 5/20/13 | 10.970 | 19.9 | 7.4 | 128 | 132 |  | 1.0 | 21.4 | 6.8 | 3 | 3 |  | 6.2 |
| 5/21/13 | 12.313 | 19.0 | 7.5 | 132 | 137 |  | 1.2 | 19.9 | 6.9 | 4 | 3 | 0.8 | 6.3 |
| 5/22/13 | 11.349 | 18.4 | 7.5 | 124 | 119 |  | 0.8 | 19.2 | 6.9 | 3 | 2 |  | 6.3 |
| 5/23/13 | 16.890 | 17.3 | 7.1 | 212 | 140 | 30.6 | 1.0 | 18.8 | 6.9 | 8 | 5 | 0.7 | 5.1 |
| 5/24/13 | 12.487 | 18.2 | 7.5 |  |  |  | 1.1 | 19.2 | 7.0 |  |  |  | 6.5 |
| 5/25/13 | 11.162 | 17.9 | 7.4 |  |  |  | 1.2 | 19.5 | 7.0 |  |  |  | 6.3 |
| 5/26/13 | 10.583 | 17.3 | 7.5 | 104 | 148 | 24.8 | 1.1 | 18.0 | 7.0 | 3 | 3 | 0.2 | 6.3 |
| 5/27/13 | 11.111 | 18.0 | 7.4 | 128 | 170 |  | 1.4 | 19.3 | 7.1 | 4 | 2 |  | 6.2 |
| 5/28/13 | 10.470 | 18.7 | 7.3 | 136 | 169 |  | 1.3 | 20.2 | 6.9 | 3 | 2 | 0.6 | 6.0 |
| 5/29/13 | 10.671 | 18.5 | 7.3 | 144 | 161 |  | 1.4 | 20.0 | 6.9 | 4 | 2 |  | 6.2 |
| 5/30/13 | 10.965 | 19.0 | 7.4 | 152 | 171 | 25.8 | 1.4 | 20.3 | 7.0 | 5 | 3 | 0.6 | 6.3 |
| 5/31/13 | 12.052 | 19.1 | 7.4 |  |  |  | 1.3 | 20.6 | 6.9 |  |  |  | 6.3 |
| 6/1/13 | 26.641 | 16.5 | 7.3 |  |  |  | 2.9 | 18.0 | 6.9 |  |  |  | 6.0 |
| 6/2/13 | 13.584 | 17.5 | 7.4 | 84 | 119 | 15.3 | 1.6 | 19.5 | 7.1 | 14 | 4 | 0.3 | 6.3 |
| 6/3/13 | 12.014 | 18.5 | 7.5 | 124 | 133 |  | 1.5 | 19.7 | 6.9 | 3 | 3 |  | 6.9 |
| 6/4/13 | 19.054 | 19.0 | 7.3 | 140 | 87 |  | 2.7 | 19.5 | 7.1 | 5 | 4 | 0.4 | 5.9 |
| 6/5/13 | 14.720 | 19.2 | 7.4 | 120 | 128 |  | 1.1 | 20.0 | 7.0 | 3 | 2 |  | 5.5 |
| 6/6/13 | 12.728 | 19.1 | 7.4 | 124 | 198 | 17.5 | 1.2 | 20.1 | 7.1 | 2 | 2 | 0.3 | 6.1 |
| 6/7/13 | 11.391 | 19.6 | 7.4 |  |  |  | 1.4 | 20.7 | 7.1 |  |  |  | 6.2 |
| 6/8/13 | 11.091 | 19.4 | 7.3 |  |  |  | 1.2 | 21.2 | 7.0 |  |  |  | 6.1 |
| 6/9/13 | 11.238 | 20.0 | 7.4 | 112 | 132 | 19.9 | 1.3 | 21.3 | 7.0 | 3 | 2 | 0.1 | 5.9 |
| 6/10/13 | 11.206 | 20.0 | 7.3 | 120 | 143 |  | 1.0 | 21.4 | 7.1 | 3 | 2 |  | 6.2 |
| 6/11/13 | 10.961 | 20.2 | 7.3 | 116 | 137 |  | 1.0 | 21.9 | 7.1 | 3 | 3 | 0.4 | 6.2 |
| 6/12/13 | 10.559 | 20.0 | 7.3 | 140 | 151 |  | 1.0 | 22.2 | 7.1 | 2 | 2 |  | 6.0 |
| 6/13/13 | 10.256 | 20.4 | 7.3 | 140 | 173 | 18.6 | 1.1 | 22.7 | 7.0 | 2 | 2 | 0.3 | 5.9 |
| 6/14/13 | 10.018 | 20.6 | 7.3 |  |  |  | 1.1 | 22.9 | 6.9 |  |  |  | 6.0 |
| 6/15/13 | 10.794 | 20.0 | 7.1 |  |  |  | 1.1 | 21.6 | 6.9 |  |  |  | 6.1 |
| 6/16/13 | 10.035 | 20.5 | 7.2 | 164 | 166 | 18.3 | 1.0 | 22.5 | 6.7 | 2 | 3 | 0.6 | 6.2 |
| 6/17/13 | 13.555 | 20.3 | 7.2 | 128 | 127 |  | 1.1 | 21.8 | 6.9 | 2 | 2 |  | 5.9 |
| 6/18/13 | 10.600 | 20.7 | 7.3 | 132 | 275 |  | 0.8 | 22.0 | 6.9 | 2 | 4 | 0.2 | 6.1 |
| 6/19/13 | 10.499 | 20.6 | 7.3 | 180 | 126 |  | 1.0 | 22.3 | 7.0 | 1 | 2 |  | 6.0 |
| 6/20/13 | 10.507 | 21.2 | 7.3 | 148 | 153 | 20.5 | 1.0 | 22.5 | 7.1 | 2 | 2 | 0.3 | 6.1 |
| 6/21/13 | 10.102 | 21.2 | 7.3 |  |  |  | 0.9 | 23.4 | 7.1 |  |  |  | 6.3 |
| 6/22/13 | 9.921 | 21.2 | 7.2 |  |  |  | 1.0 | 23.2 | 7.1 |  |  |  | 6.1 |
| 6/23/13 | 9.742 | 21.5 | 7.2 | 144 | 174 | 17.7 | 1.1 | 23.1 | 7.1 | 2 | 2 | 0.1 | 6.4 |
| 6/24/13 | 9.951 | 21.3 | 7.2 | 128 | 154 |  | 1.0 | 23.1 | 7.0 | 3 | 2 |  | 6.1 |
| 6/25/13 | 10.031 | 21.0 | 7.2 | 152 | 156 |  | 1.1 | 23.0 | 7.0 | 3 | 2 | 0.3 | 6.1 |
| 6/26/13 | 10.086 | 21.2 | 7.2 | 140 | 160 |  | 0.9 | 23.1 | 7.1 | 3 | 3 |  | 6.0 |
| 6/27/13 | 9.951 | 21.4 | 7.2 | 144 | 175 | 18.5 | 1.0 | 23.8 | 7.0 | 3 | 3 | 0.2 | 6.1 |
| 6/28/13 | 9.717 | 21.6 | 7.3 |  |  |  | 1.2 | 23.8 | 7.1 |  |  |  | 6.1 |
| 6/29/13 | 9.545 | 21.5 | 7.1 |  |  |  | 1.2 | 23.4 | 7.0 |  |  |  | 6.6 |
| 6/30/13 | 9.117 | 21.5 | 7.1 | 156 | 132 | 26.2 | 1.2 | 23.2 | 7.0 | 3 | 2 | 0.1 | 6.0 |
| 7/1/13 | 9.406 | 21.3 | 7.2 |  | 147 |  | 0.9 | 22.6 | 7.1 |  | 3 |  | 6.0 |
| 7/2/13 | 9.158 | 19.5 | 7.1 | 152 | 104 |  | 0.8 | 20.2 | 7.0 | 2 | 3 | 0.2 | 5.8 |
| 7/3/13 | 8.865 | 21.6 | 7.1 | 124 | 133 |  | 0.8 | 23.0 | 7.1 | 2 | 2 |  | 5.1 |
| 7/4/13 | 8.407 | 21.2 | 7.2 | 132 | 152 | 17.5 | 1.1 | 23.4 | 7.0 | 1 | 2 | 0.2 | 5.8 |
| 7/5/13 | 8.633 | 21.3 | 7.2 | 128 |  |  | 1.1 | 22.8 | 7.0 | 2 |  |  | 5.7 |
| 7/6/13 | 9.079 | 22.0 | 7.2 |  |  |  | 1.0 | 23.2 | 7.0 |  |  |  | 5.8 |
| 7/7/13 | 8.490 | 22.0 | 7.1 | 116 | 122 | 31.9 | 0.9 | 24.8 | 7.0 | 2 | 2 | 0.1 | 5.8 |
| 7/8/13 | 9.532 | 22.3 | 7.0 | 152 | 130 |  | 0.9 | 24.1 | 6.9 | 2 | 2 |  | 5.9 |
| 7/9/13 | 9.503 | 22.3 | 7.0 | 136 | 185 |  | 0.6 | 24.3 | 6.9 | 2 | 2 | 0.1 | 5.9 |
| 7/10/13 | 9.285 | 22.6 | 7.2 | 120 | 127 |  | 1.0 | 24.8 | 6.9 | 2 | 2 |  | 5.7 |
| 7/11/13 | 9.154 | 22.2 | 7.1 | 128 | 152 | 28.5 | 1.0 | 24.3 | 6.9 | 2 | 2 | 0.1 | 5.6 |
| 7/12/13 | 9.221 | 22.7 | 7.0 |  |  |  | 0.8 | 24.4 | 6.9 |  |  |  | 5.7 |
| 7/13/13 | 9.002 | 22.8 | 7.1 |  |  |  | 0.9 | 24.2 | 6.9 |  |  |  | 5.7 |
| 7/14/13 | 11.575 | 23.3 | 6.9 | 272 | 132 | 24.1 | 0.8 | 24.5 | 6.9 | 2 | 3 | 0.2 | 5.7 |
| 7/15/13 | 14.467 | 21.3 | 6.8 | 296 | 170 |  | 1.6 | 22.1 | 6.8 | 5 | 3 |  | 5.5 |
| 7/16/13 | 11.535 | 21.8 | 7.2 | 136 | 103 |  | 1.4 | 22.6 | 6.9 | 3 | 2 | 0.3 | 6.2 |
| 7/17/13 | 14.980 | 22.0 | 7.2 | 140 | 109 |  | 1.5 | 23.0 | 7.0 | 3 | 2 |  | 6.1 |
| 7/18/13 | 11.424 | 22.0 | 7.2 | 144 | 176 | 20.5 | 1.6 | 23.3 | 7.0 | 2 | 2 | 0.2 | 6.2 |
| 7/19/13 | 10.432 | 22.4 | 7.2 |  |  |  | 1.5 | 23.8 | 7.1 |  |  |  | 6.0 |
| 7/20/13 | 10.153 | 22.5 | 7.2 |  |  |  | 1.3 | 24.5 | 7.1 |  |  |  | 6.0 |
| 7/21/13 | 9.873 | 24.5 | 7.2 | 140 | 124 | 24.6 | 1.3 | 25.5 | 7.1 | 1 | 3 | 0.3 | 6.1 |
| 7/22/13 | 10.297 | 22.3 | 7.1 | 112 | 160 |  | 1.0 | 24.4 | 7.1 | 2 | 2 |  | 5.8 |
| 7/23/13 | 10.028 | 23.0 | 7.2 | 96 | 59 |  | 1.6 | 24.5 | 6.9 | 2 | 2 | 0.4 | 5.5 |
| 7/24/13 | 11.020 | 22.5 | 7.0 | 152 | 168 |  | 1.2 | 24.0 | 6.8 | 1 | 2 |  | 5.8 |
| 7/25/13 | 9.985 | 22.3 | 7.2 | 216 | 155 | 27.4 | 1.0 | 24.4 | 7.0 | 3 | 2 | 0.9 | 5.8 |
| 7/26/13 | 23.781 | 21.3 | 6.8 |  |  |  | 2.4 | 22.2 | 6.7 |  |  |  | 5.1 |
| 7/27/13 | 14.430 | 24.0 | 7.1 |  |  |  | 1.2 | 25.1 | 7.0 |  |  |  | 5.9 |
| 7/28/13 | 12.932 | 24.9 | 7.4 | 88 | 110 | 23.7 | 1.1 | 25.3 | 7.1 | 2 | 2 | 0.3 | 5.7 |
| 7/29/13 | 13.398 | 22.5 | 7.3 | 104 | 103 |  | 1.2 | 23.7 | 7.1 | 2 | 2 |  | 5.9 |
| 7/30/13 | 14.008 | 22.7 | 7.2 | 92 | 93 |  | 1.1 | 24.0 | 7.0 | 2 | 2 | 0.8 | 6.1 |
| 7/31/13 | 11.882 | 22.6 | 7.3 | 92 | 168 |  | 0.9 | 24.5 | 7.0 | 2 | 2 |  | 5.9 |
| 8/1/13 | 11.393 | 23.0 | 7.3 | 108 | 195 | 20.5 | 1.2 | 24.3 | 7.0 | 2 | 2 | 0.2 | 6.0 |
| 8/2/13 | 10.851 | 23.2 | 7.2 |  |  |  | 0.9 | 24.8 | 7.0 |  |  |  | 5.9 |
| 8/3/13 | 10.509 | 23.1 | 7.2 |  |  |  | 1.0 | 24.8 | 6.9 |  |  |  | 5.9 |
| 8/4/13 | 10.279 | 22.5 | 7.1 | 116 | 176 | 25.1 | 1.1 | 24.9 | 6.9 | 2 | 2 | 0.2 | 6.0 |
| 8/5/13 | 10.767 | 23.1 | 7.1 | 124 | 195 |  | 1.0 | 24.8 | 7.0 | 2 | 2 |  | 6.0 |
| 8/6/13 | 10.392 | 23.3 | 7.1 | 132 | 211 |  | 1.0 | 25.1 | 7.0 | 3 | 4 | 0.4 | 5.7 |
| 8/7/13 | 10.293 | 23.1 | 7.1 | 140 | 198 |  | 1.0 | 24.9 | 7.0 | 3 | 3 |  | 5.5 |
| 8/8/13 | 10.403 | 23.0 | 7.1 | 196 | 243 | 20.8 | 0.9 | 24.3 | 6.9 | 3 | 2 | 0.1 | 5.7 |
| 8/9/13 | 13.234 | 23.1 | 7.0 |  |  |  | 1.2 | 24.2 | 6.8 |  |  |  | 5.9 |
| 8/10/13 | 10.410 | 23.3 | 7.2 |  |  |  | 1.3 | 24.2 | 6.9 |  |  |  | 5.9 |
| 8/11/13 | 10.185 | 23.5 | 7.1 | 108 | 191 | 24.3 | 1.1 | 24.6 | 7.0 | 2 | 2 | 1.6 | 5.9 |
| 8/12/13 | 10.500 | 23.3 | 7.1 | 104 | 199 |  | 1.1 | 24.7 | 7.0 | 1 | 2 |  | 5.6 |
| 8/13/13 | 13.672 | 22.7 | 6.9 | 176 | 181 |  | 1.1 | 23.8 | 6.9 | 2 | 2 | 0.7 | 5.2 |
| 8/14/13 | 11.269 | 23.0 | 7.2 | 108 | 151 |  | 1.1 | 23.7 | 6.9 | 2 | 2 |  | 5.8 |
| 8/15/13 | 10.694 | 22.6 | 7.2 | 124 | 198 | 22.1 | 1.1 | 23.8 | 7.0 | 2 | 2 | 0.5 | 5.9 |
| 8/16/13 | 12.756 | 22.5 | 7.3 |  |  |  | 1.2 | 23.9 | 7.0 |  |  |  | 5.7 |
| 8/17/13 | 11.270 | 22.5 | 7.2 |  |  |  | 1.2 | 24.0 | 7.0 |  |  |  | 5.9 |
| 8/18/13 | 11.061 | 23.0 | 7.2 | 104 | 238 | 23.3 | 1.1 | 24.5 | 7.0 | 2 | 2 | 0.3 | 5.9 |
| 8/19/13 | 11.315 | 22.8 | 7.2 | 112 | 206 |  | 1.1 | 23.9 | 7.0 | 2 | 2 |  | 5.9 |
| 8/20/13 | 10.912 | 22.9 | 7.2 | 120 | 189 |  | 1.0 | 24.3 | 7.0 | 2 | 3 | 0.3 | 5.9 |
| 8/21/13 | 10.612 | 23.2 | 7.2 | 120 | 198 |  | 0.8 | 24.5 | 7.0 | 2 | 2 |  | 5.9 |
| 8/22/13 | 10.437 | 23.0 | 7.2 | 132 | 203 | 19.0 | 0.8 | 24.5 | 6.7 | 2 | 2 | 0.2 | 5.9 |
| 8/23/13 | 10.424 | 23.2 | 7.2 |  |  |  | 0.9 | 24.8 | 7.0 |  |  |  | 5.8 |
| 8/24/13 | 10.425 | 23.5 | 7.2 |  |  |  | 1.0 | 25.0 | 7.0 |  |  |  | 6.0 |
| 8/25/13 | 10.490 | 23.5 | 7.2 | 112 | 216 | 24.9 | 1.0 | 25.2 | 7.0 | 2 | 2 | 0.5 | 5.8 |
| 8/26/13 | 10.506 | 23.3 | 7.1 | 148 | 258 |  | 1.1 | 24.8 | 6.9 | 3 | 2 |  | 5.9 |
| 8/27/13 | 10.385 | 23.0 | 7.2 | 140 | 221 |  | 0.9 | 24.7 | 7.0 | 3 | 2 | 0.5 | 5.8 |
| 8/28/13 | 10.330 | 23.2 | 7.2 | 200 | 212 |  | 0.8 | 24.5 | 7.0 | 3 | 3 |  | 5.7 |
| 8/29/13 | 10.108 | 23.2 | 7.2 | 136 | 222 | 19.8 | 0.8 | 24.6 | 7.1 | 3 | 2 | 0.4 | 5.6 |
| 8/30/13 | 10.058 | 23.3 | 7.1 |  |  |  | 1.6 | 25.0 | 7.0 |  |  |  | 5.9 |
| 8/31/13 | 10.119 | 23.8 | 7.3 |  |  |  | 1.3 | 24.6 | 7.0 |  |  |  | 5.8 |
| 9/1/13 | 9.622 | 23.7 | 7.3 | 140 | 341 | 27.3 | 1.3 | 24.5 | 7.0 | 2 | 2 | 0.1 | 5.9 |
| 9/2/13 | 10.596 | 23.8 | 7.2 | 144 | 218 |  | 1.2 | 24.3 | 7.0 | 3 | 2 |  | 5.8 |
| 9/3/13 | 9.970 | 23.1 | 7.2 | 140 | 235 |  | 1.2 | 24.2 | 6.9 | 2 | 3 | 0.5 | 5.2 |
| 9/4/13 | 9.760 | 23.5 | 7.1 | 128 | 258 |  | 0.7 | 24.7 | 7.0 | 3 | 2 |  | 5.1 |
| 9/5/13 | 9.710 | 23.2 | 7.2 | 152 | 261 | 14.4 | 1.0 | 24.6 | 6.9 | 2 | 2 | 0.3 | 5.6 |
| 9/6/13 | 9.627 | 23.4 | 7.2 |  |  |  | 0.9 | 24.9 | 7.0 |  |  |  | 5.6 |
| 9/7/13 | 9.513 | 23.0 | 7.1 |  |  |  | 1.3 | 25.0 | 6.8 |  |  |  | 6.2 |
| 9/8/13 | 10.382 | 24.0 | 7.2 | 128 | 213 | 27.0 | 1.1 | 25.4 | 6.9 | 4 | 4 | 0.8 | 5.9 |
| 9/9/13 | 9.670 | 23.5 | 7.1 | 128 | 232 |  | 0.9 | 24.9 | 6.9 | 5 | 3 |  | 5.8 |
| 9/10/13 | 9.692 | 23.3 | 7.2 | 156 | 230 |  | 0.9 | 24.8 | 7.0 | 4 | 3 | 0.3 | 5.6 |
| 9/11/13 | 9.681 | 23.5 | 7.2 | 136 | 218 |  | 0.9 | 25.0 | 6.9 | 4 | 4 |  | 5.9 |
| 9/12/13 | 9.853 | 23.4 | 7.2 | 180 | 244 | 11.8 | 0.9 | 25.1 | 6.9 | 4 | 3 | 0.2 | 5.5 |
| 9/13/13 | 9.845 | 23.6 | 7.2 |  |  |  | 0.8 | 24.8 | 6.9 |  |  |  | 5.5 |
| 9/14/13 | 9.551 | 25.5 | 7.2 |  |  |  | 1.1 | 26.3 | 6.8 |  |  |  | 5.7 |
| 9/15/13 | 9.653 | 23.0 | 7.2 | 144 | 245 | 28.7 | 0.7 | 24.0 | 6.9 | 3 | 3 | 0.1 | 5.6 |
| 9/16/13 | 9.609 | 23.2 | 7.2 | 148 | 251 |  | 1.1 | 24.2 | 6.7 | 2 | 2 |  | 6.6 |
| 9/17/13 | 9.767 | 23.0 | 7.2 | 136 | 186 |  | 1.2 | 24.5 | 6.7 | 3 | 2 | 0.2 | 6.1 |
| 9/18/13 | 9.642 | 23.4 | 7.2 | 160 | 249 |  | 0.8 | 24.7 | 7.0 | 3 | 2 |  | 5.7 |
| 9/19/13 | 10.796 | 23.2 | 7.2 | 260 | 249 | 25.4 | 1.1 | 24.5 | 7.0 | 3 | 2 | 0.4 | 5.6 |
| 9/20/13 | 9.885 | 22.8 | 7.3 |  |  |  | 0.9 | 23.2 | 6.8 |  |  |  | 5.6 |
| 9/21/13 | 9.114 | 24.5 | 7.2 |  |  |  | 1.1 | 26.2 | 6.9 |  |  |  | 5.9 |
| 9/22/13 | 9.246 | 24.5 | 7.2 | 132 | 216 | 26.8 | 1.0 | 25.0 | 6.9 | 4 | 3 | 0.2 | 5.8 |
| 9/23/13 | 9.606 | 22.4 | 7.2 | 144 | 274 |  | 1.1 | 23.2 | 7.0 | 3 | 2 |  | 5.7 |
| 9/24/13 | 9.276 | 22.8 | 7.1 | 176 | 221 |  | 1.0 | 23.3 | 7.0 | 2 | 2 | 0.1 | 5.7 |
| 9/25/13 | 9.162 | 22.6 | 7.3 | 128 | 226 |  | 0.7 | 23.5 | 7.0 | 3 | 3 |  | 5.4 |
| 9/26/13 | 9.500 | 22.8 | 7.2 | 188 | 257 | 24.5 | 0.8 | 23.9 | 7.0 | 3 | 2 | 0.3 | 5.8 |
| 9/27/13 | 9.119 | 23.2 | 7.3 |  |  |  | 0.6 | 23.8 | 7.0 |  |  |  | 5.8 |
| 9/28/13 | 12.131 | 23.2 | 6.5 |  |  |  | 0.9 | 24.5 | 6.8 |  |  |  | 5.8 |
| 9/29/13 | 9.597 | 21.5 | 7.3 | 128 | 217 | 24.9 | 1.2 | 22.2 | 6.7 | 3 | 3 | 0.3 | 6.1 |
| 9/30/13 | 9.492 | 22.2 | 7.2 | 132 | 239 |  | 1.0 | 22.8 | 6.9 | 3 | 2 |  | 5.8 |
| 10/1/13 | 9.451 | 22.5 | 7.3 | 124 | 244 |  | 1.0 | 23.3 | 6.9 | 2 | 2 | 0.4 | 6.0 |
| 10/2/13 | 9.863 | 22.7 | 7.1 | 152 | 232 |  | 0.8 | 23.4 | 6.9 | 3 | 2 |  | 6.0 |
| 10/3/13 | 9.639 | 22.4 | 7.2 | 136 | 229 | 17.6 | 1.2 | 23.7 | 6.8 | 2 | 2 | 0.1 | 6.0 |
| 10/4/13 | 9.625 | 22.7 | 7.1 |  |  |  | 1.0 | 23.8 | 6.9 |  |  |  | 5.8 |
| 10/5/13 | 10.599 | 20.4 | 7.2 |  |  |  | 1.1 | 21.5 | 6.8 |  |  |  | 5.1 |
| 10/6/13 | 9.630 | 21.2 | 7.1 | 148 | 241 | 29.0 | 0.7 | 21.1 | 6.9 | 2 | 2 | 0.1 | 6.2 |
| 10/7/13 | 9.312 | 21.6 | 7.3 | 196 | 254 |  | 1.0 | 21.9 | 6.9 | 3 | 3 |  | 5.7 |
| 10/8/13 | 9.202 | 21.8 | 7.2 | 144 | 250 |  | 0.9 | 22.0 | 6.8 | 2 | 2 | 0.3 | 5.7 |
| 10/9/13 | 9.490 | 20.5 | 7.2 | 140 | 250 |  | 1.0 | 21.0 | 6.9 | 2 | 2 |  | 6.0 |
| 10/10/13 | 9.172 | 20.9 | 7.1 | 136 | 248 | 27.2 | 1.0 | 21.3 | 6.9 | 3 | 3 | 0.2 | 5.8 |
| 10/11/13 | 8.619 | 20.9 | 7.2 |  |  |  | 1.0 | 21.4 | 7.0 |  |  |  | 5.8 |
| 10/12/13 | 8.254 | 20.1 | 7.2 |  |  |  | 1.1 | 21.2 | 6.9 |  |  |  | 5.9 |
| 10/13/13 | 8.836 | 20.4 | 7.2 | 128 | 254 | 28.1 | 1.1 | 21.0 | 6.9 | 1 | 2 | 0.1 | 5.9 |
| 10/14/13 | 11.234 | 20.0 | 7.2 | 152 | 222 |  | 1.1 | 20.5 | 6.9 | 10 | 2 |  | 5.9 |
| 10/15/13 | 12.190 | 19.0 | 7.4 | 124 | 290 |  | 1.3 | 19.0 | 6.9 | 2 | 7 | 0.1 | 6.3 |
| 10/16/13 | 9.700 | 19.3 | 7.4 | 156 | 286 |  | 0.9 | 18.8 | 6.9 | 2 | 4 |  | 6.0 |
| 10/17/13 | 9.375 | 19.2 | 7.4 | 124 | 303 | 22.2 | 1.0 | 19.0 | 6.9 | 2 | 6 | 0.2 | 6.2 |
| 10/18/13 | 9.340 | 18.9 | 7.2 |  |  |  | 1.2 | 19.1 | 6.9 |  |  |  | 6.0 |
| 10/19/13 | 9.030 | 18.5 | 7.3 |  |  |  | 1.3 | 19.2 | 6.9 |  |  |  | 6.2 |
| 10/20/13 | 9.375 | 20.2 | 7.2 | 132 | 221 | 29.0 | 0.9 | 22.3 | 6.9 | 2 | 2 | 0.4 | 5.7 |
| 10/21/13 | 11.442 | 18.0 | 7.2 | 144 | 212 |  | 1.2 | 18.5 | 7.0 | 2 | 2 |  | 6.1 |
| 10/22/13 | 9.615 | 19.1 | 7.3 | 136 | 264 |  | 1.1 | 18.8 | 7.0 | 2 | 2 | 0.4 | 6.2 |
| 10/23/13 | 9.304 | 19.0 | 7.3 | 140 | 267 |  | 1.0 | 18.9 | 7.0 | 3 | 2 |  | 6.0 |
| 10/24/13 | 9.246 | 18.9 | 7.3 | 140 | 284 | 34.3 | 0.9 | 18.8 | 7.0 | 2 | 4 | 0.6 | 6.0 |
| 10/25/13 | 9.076 | 18.7 | 7.2 |  |  |  | 1.1 | 18.1 | 6.9 |  |  |  | 6.0 |
| 10/26/13 | 9.966 | 17.3 | 7.1 |  |  |  | 1.3 | 18.0 | 6.9 |  |  |  | 6.1 |
| 10/27/13 | 9.627 | 19.3 | 7.2 | 124 | 246 | 26.9 | 1.0 | 22.0 | 7.0 | 2 | 3 | 0.1 | 5.3 |
| 10/28/13 | 9.595 | 18.6 | 7.3 | 132 | 248 |  | 1.2 | 18.8 | 6.9 | 2 | 3 |  | 5.8 |
| 10/29/13 | 9.550 | 18.9 | 7.2 | 144 | 241 |  | 1.1 | 19.3 | 6.9 | 2 | 2 | 0.4 | 5.9 |
| 10/30/13 | 10.627 | 18.9 | 7.1 | 164 | 236 |  | 0.7 | 19.4 | 7.0 | 2 | 2 |  | 5.7 |
| 10/31/13 | 10.842 | 18.0 | 7.3 | 120 | 185 | 35.4 | 1.2 | 18.2 | 6.8 | 6 | 8 | 0.2 | 5.9 |
| 11/1/13 | 9.589 | 18.3 | 7.3 |  |  |  | 1.0 | 18.1 | 7.0 |  |  |  | 6.1 |
| 11/2/13 | 9.180 | 17.6 | 7.3 |  |  |  | 1.0 | 18.0 | 6.9 |  |  |  | 6.1 |
| 11/3/13 | 9.646 | 17.4 | 7.2 | 160 | 219 | 28.4 | 1.0 | 18.1 | 6.9 | 2 | 2 | 0.7 | 5.9 |
| 11/4/13 | 9.646 | 17.9 | 7.3 | 152 | 249 |  | 1.0 | 17.7 | 6.9 | 3 | 2 |  | 6.0 |
| 11/5/13 | 10.019 | 18.0 | 7.1 | 144 | 222 |  | 1.0 | 17.8 | 6.9 | 5 | 5 | 0.3 | 6.0 |
| 11/6/13 | 15.271 | 16.5 | 7.4 | 112 | 205 |  | 1.2 | 16.0 | 6.8 | 4 | 3 |  | 6.2 |
| 11/7/13 | 10.061 | 17.8 | 7.5 | 148 | 262 | 27.6 | 1.5 | 16.8 | 6.8 | 3 | 2 | 0.3 | 6.3 |
| 11/8/13 | 9.740 | 17.2 | 7.4 |  |  |  | 1.7 | 16.7 | 6.9 |  |  |  | 6.4 |
| 11/9/13 | 9.457 | 16.8 | 7.3 |  |  |  | 1.1 | 17.5 | 6.9 |  |  |  | 6.1 |
| 11/10/13 | 9.597 | 17.8 | 7.2 | 136 | 249 | 27.4 | 1.2 | 18.8 | 7.0 | 3 | 2 | 0.1 | 6.0 |
| 11/11/13 | 9.456 | 17.2 | 7.3 | 120 | 219 |  | 1.2 | 18.0 | 6.9 | 3 | 3 |  | 6.1 |
| 11/12/13 | 9.396 | 16.9 | 7.3 | 112 | 232 |  | 1.6 | 15.9 | 7.0 | 6 | 17 | 0.6 | 6.4 |
| 11/13/13 | 9.633 | 16.8 | 7.3 | 128 | 240 |  | 1.1 | 16.0 | 7.0 | 4 | 3 |  | 6.3 |
| 11/14/13 | 9.668 | 16.9 | 7.3 | 188 | 289 | 22.3 | 1.1 | 15.9 | 7.0 | 4 | 2 | 0.8 | 6.4 |
| 11/15/13 | 9.204 | 17.1 | 7.2 |  |  |  | 1.3 | 16.8 | 7.0 |  |  |  | 6.4 |
| 11/16/13 | 9.780 | 17.6 | 7.3 |  |  |  | 1.1 | 18.2 | 7.0 |  |  |  | 6.3 |
| 11/17/13 | 9.487 | 21.3 | 7.3 | 148 | 261 | 31.8 | 1.0 | 21.5 | 6.9 | 3 | 3 | 2.5 | 6.0 |
| 11/18/13 | 9.147 | 21.3 | 7.3 | 160 | 234 |  | 1.3 | 20.9 | 7.0 | 3 | 2 |  | 6.1 |
| 11/19/13 | 9.137 | 21.0 | 7.2 | 152 | 257 |  | 1.0 | 20.7 | 7.0 | 4 | 3 | 0.9 | 6.2 |
| 11/20/13 | 9.245 | 20.8 | 7.0 | 148 | 267 |  | 1.1 | 20.3 | 7.0 | 5 | 4 |  | 6.1 |
| 11/21/13 | 9.231 | 21.1 | 7.3 | 160 | 238 | 30.5 | 0.9 | 21.2 | 6.9 | 5 | 2 | 0.7 | 5.3 |
| 11/22/13 | 9.105 | 19.6 | 7.4 |  |  |  | 1.1 | 18.1 | 7.0 |  |  |  | 6.3 |
| 11/23/13 | 9.699 | 18.2 | 7.3 |  |  |  | 1.0 | 18.6 | 7.0 |  |  |  | 6.4 |
| 11/24/13 | 9.752 | 17.0 | 7.4 | 124 | 256 | 26.9 | 1.0 | 17.9 | 6.9 | 5 | 2 | 1.3 | 6.4 |
| 11/25/13 | 9.957 | 19.4 | 7.3 | 148 | 246 |  | 1.1 | 18.3 | 6.9 | 3 | 4 |  | 6.2 |
| 11/26/13 | 9.500 | 19.4 | 7.3 | 112 | 233 |  | 1.2 | 18.4 | 7.0 | 4 | 2 | 1.4 | 6.4 |
| 11/27/13 | 9.005 | 19.0 | 7.3 | 136 | 259 |  | 1.3 | 18.3 | 6.9 | 4 | 2 |  | 6.3 |
| 11/28/13 | 8.221 | 19.0 | 7.3 | 116 | 239 | 25.6 | 1.1 | 18.5 | 6.9 | 3 | 2 | 0.4 | 6.3 |
| 11/29/13 | 7.971 | 18.7 | 7.3 |  |  |  | 1.5 | 18.2 | 6.8 |  |  |  | 6.6 |
| 11/30/13 | 8.566 | 19.0 | 7.2 |  |  |  | 1.1 | 18.5 | 6.8 |  |  |  | 6.4 |
| 12/1/13 | 8.917 | 18.0 | 7.2 | 136 | 264 | 29.1 | 1.2 | 18.3 | 6.8 | 4 | 2 | 0.7 | 6.4 |
| 12/2/13 | 9.277 | 19.3 | 7.3 | 164 | 293 |  | 1.4 | 19.0 | 6.8 | 4 | 2 |  | 6.2 |
| 12/3/13 | 9.196 | 19.0 | 7.2 | 184 | 268 |  | 1.1 | 19.2 | 6.9 | 4 | 3 | 0.6 | 6.3 |
| 12/4/13 | 9.101 | 19.4 | 7.3 | 188 | 273 |  | 1.5 | 18.4 | 7.0 | 4 | 2 |  | 6.3 |
| 12/5/13 | 9.407 | 18.1 | 7.3 | 156 | 272 | 27.5 | 1.2 | 16.3 | 6.9 | 4 | 2 | 0.6 | 6.6 |
| 12/6/13 | 9.555 | 17.4 | 7.3 |  |  |  | 1.4 | 15.7 | 7.0 |  |  |  | 6.5 |
| 12/7/13 | 9.835 | 17.4 | 7.4 |  |  |  | 1.3 | 15.9 | 6.9 |  |  |  | 6.5 |
| 12/8/13 | 10.236 | 17.0 | 7.3 | 144 | 263 | 31.2 | 1.3 | 16.2 | 6.9 | 4 | 3 | 0.5 | 6.5 |
| 12/9/13 | 9.894 | 17.6 | 7.2 | 152 | 278 |  | 1.2 | 16.0 | 6.9 | 4 | 2 |  | 6.5 |
| 12/10/13 | 9.905 | 18.1 | 7.3 | 156 | 261 |  | 1.5 | 15.9 | 7.0 | 5 | 5 | 0.5 | 6.6 |
| 12/11/13 | 9.662 | 17.3 | 7.3 | 132 | 269 |  | 1.3 | 17.0 | 6.9 | 4 | 2 |  | 6.6 |
| 12/12/13 | 9.702 | 18.0 | 7.3 | 140 | 283 | 23.0 | 1.2 | 16.9 | 7.0 | 4 | 2 | 0.4 | 6.8 |
| 12/13/13 | 9.697 | 18.2 | 7.2 |  |  |  | 1.0 | 17.3 | 7.0 |  |  |  | 6.2 |
| 12/14/13 | 9.432 | 17.3 | 7.2 |  |  |  | 1.2 | 16.8 | 7.0 |  |  |  | 6.6 |
| 12/15/13 | 9.192 | 18.4 | 7.3 | 156 | 272 | 26.3 | 1.1 | 17.5 | 7.0 | 3 | 2 | 0.4 | 6.6 |
| 12/16/13 | 8.826 | 18.5 | 7.2 | 123 | 283 |  | 1.4 | 18.3 | 6.9 | 3 | 2 |  | 6.6 |
| 12/17/13 | 8.814 | 18.6 | 7.3 | 124 | 254 |  | 1.5 | 18.4 | 7.0 | 3 | 3 | 0.5 | 6.6 |
| 12/18/13 | 8.780 | 18.5 | 7.4 | 148 | 250 |  | 1.5 | 18.5 | 7.0 | 3 | 3 |  | 6.5 |
| 12/19/13 | 8.743 | 18.5 | 7.3 | 244 | 284 | 27.8 | 1.2 | 18.3 | 7.1 | 3 | 2 | 0.3 | 6.7 |
| 12/20/13 | 8.789 | 17.7 | 7.2 |  |  |  | 1.4 | 16.9 | 7.0 |  |  |  | 6.5 |
| 12/21/13 | 15.215 | 15.0 | 7.2 |  |  |  | 1.7 | 15.9 | 7.1 |  |  |  | 5.8 |
| 12/22/13 | 10.862 | 15.7 | 7.2 | 92 | 241 | 18.9 | 1.6 | 15.0 | 7.0 | 4 | 2 | 0.6 | 5.9 |
| 12/23/13 | 10.010 | 16.6 | 7.4 | 108 | 213 |  | 1.6 | 15.8 | 7.0 | 4 | 3 |  | 6.9 |
| 12/24/13 | 10.027 | 16.2 | 7.4 | 132 | 225 |  | 1.5 | 15.5 | 7.1 | 4 | 3 | 0.7 | 6.4 |
| 12/25/13 | 9.362 | 16.0 | 7.5 | 92 | 232 |  | 1.9 | 16.5 | 6.9 | 4 | 2 |  | 5.4 |
| 12/26/13 | 9.047 | 16.8 | 7.4 | 120 | 220 | 17.5 | 1.6 | 16.6 | 7.0 | 4 | 2 | 0.5 | 6.8 |
| 12/27/13 | 8.980 | 17.2 | 7.3 |  |  |  | 1.4 | 17.1 | 7.0 |  |  |  | 6.9 |
| 12/28/13 | 8.148 | 17.4 | 7.4 |  |  |  | 1.3 | 17.2 | 7.0 |  |  |  | 6.8 |
| 12/29/13 | 8.919 | 17.2 | 7.4 | 132 | 248 | 22.7 | 1.9 | 16.6 | 7.1 | 4 | 2 | 0.4 | 5.4 |
| 12/30/13 | 9.221 | 15.8 | 7.4 | 108 | 220 |  | 1.2 | 16.2 | 6.9 | 5 | 3 |  | 6.0 |
| 12/31/13 | 9.255 | 16.2 | 7.3 | 128 | 224 |  | 1.7 | 16.4 | 6.9 | 4 | 2 | 0.4 | 6.5 |

# Appendix B: CECs (and MRLs) Analyzed

| Compound | MRL (ng/L) | Compound | MRL (ng/L) |
| --- | --- | --- | --- |
| 1,7-Dimethylxanthine | 100 | Iohexol | 1000 |
| 2,4-D | 5 | Iopromide | 5 |
| 4-nonylphenol | 100 | Isobutylparaben | 5 |
| 4-tert-Octylphenol | 50 | Isoproturon | 100 |
| Acesulfame-K | 200 | Ketoprofen | 5 |
| Acetaminophen | 500 | Ketorolac | 5 |
| Albuterol | 5 | Lidocaine | 5 |
| Amoxicillin (semi-quantitative) | 200 | Lincomycin | 10 |
| Andorostenedione | 5 | Linuron | 5 |
| Atenolol | 5 | Lopressor | 20 |
| Atrazine | 5 | Meclofenamic Acid | 5 |
| Azithromycin | 20 | Meprobamate | 5 |
| Bendroflumethiazide | 5 | Metazachlor | 5 |
| Bezafibrate | 5 | Methylparaben | 20 |
| BPA | 10 | Metolachlor | 5 |
| Bromacil | 5 | Naproxen | 10 |
| Butalbital | 5 | Nifedipine | 20 |
| Butylparaben | 5 | Norethisterone | 5 |
| Caffeine | 500 | OUST (Sulfameturon,methyl) | 5 |
| Carbadox | 5 | Oxolinic acid | 10 |
| Carbamazepine | 5 | Pentoxifylline | 5 |
| Carisoprodol | 5 | Phenazone | 5 |
| Chloramphenicol | 100 | Primidone | 50 |
| Chloridazon | 5 | Progesterone | 5 |
| Chlorotoluron | 5 | Propazine | 5 |
| Cimetidine | 5 | Propylparaben | 5 |
| Clofibric Acid | 5 | Quinoline | 5 |
| Cotinine | 10 | Salicylic Acid | 100 |
| Cyanazine | 5 | Simazine | 5 |
| DACT | 5 | Sucralose | 1000 |
| DEA | 5 | Sulfachloropyridazine | 5 |
| DEET | 100 | Sulfadiazine | 5 |
| Dehydronifedipine | 5 | Sulfadimethoxine | 5 |
| DIA | 5 | Sulfamerazine | 5 |
| Diazepam | 5 | Sulfamethazine | 5 |
| Diclofenac | 5 | Sulfamethizole | 5 |
| Dilantin | 20 | Sulfamethoxazole | 50 |
| Diltiazem | 5 | Sulfathiazole | 5 |
| Diuron | 5 | TCEP | 10 |
| Erythromycin | 10 | TCPP | 100 |
| Estradiol | 5 | TDCPP | 100 |
| Estriol | 5 | Testosterone | 5 |
| Estrone (E1) | 5 | Theobromine | 100 |
| 17β-Estradiol (E2) | 5 | Theophylline | 200 |
| Ethylparaben | 20 | Thiabendazole | 5 |
| Flumeqine | 10 | Triclocarban | 5 |
| Fluoxetine | 10 | Triclosan | 10 |
| Gemfibrozil | 50 | Trimethoprim | 50 |
| Ibuprofen | 10 | Warfarin | 5 |

# Appendix C: Stoichiometry Matrix

|  | Description | Units |
| --- | --- | --- |
| r1 | aerobic growth of heterotrophs on soluble substrate with ammonia as N source | gCOD/m3/d |
| r2 | anoxic growth of heterotrophs on soluble substrate with ammonia as N source | gCOD/m3/d |
| r3 | aerobic growth of heterotrophs on soluble substrate with nitrate as N source | gCOD/m3/d |
| r4 | anoxic growth of heterotrophs soluble substrate with nitrate as N source | gCOD/m3/d |
| r5 | decay of heterotrophs | gCOD/m3/d |
| r6 | hydrolysis of entrapped organics | gCOD/m3/d |
| r7 | hydrolysis of entrapped organic nitrogen | gCOD/m3/d |
| r8 | ammonification of soluble organic nitrogen | gN/m3/d |
| r9 | growth of autotrophs | gCOD/m3/d |
| r10 | decay of autotrophs | gCOD/m3/d |
| r11 | biodegradation of E1 | g/m3/d |
| r12 | adsorption of E1 | g/m3 |
| r13 | desorption of E1 | g/m3/d |
| r14 | biodegradation of atenolol | g/m3/d |
| r15 | adsorption of atenolol | g/m3 |
| r16 | desorption of atenolol | g/m3/d |
| r17 | biodegradation of lopressor | g/m3/d |
| r18 | adsorption of lopressor | g/m3 |
| r19 | desorption of lopressor | g/m3/d |
| r20 | biodegradation of meprobamate | g/m3/d |
| r21 | adsorption of meprobamate | g/m3 |
| r22 | desorption of meprobamate | g/m3/d |
| r23 | biodegradation of triclosan | g/m3/d |
| r24 | adsorption of triclosan | g/m3 |
| r25 | desorption of triclosan | g/m3/d |
| r26 | biodegradation of gemfibrozil | g/m3/d |
| r27 | adsorption of gemfibrozil | g/m3 |
| r28 | desorption of gemfibrozil | g/m3/d |
| r29 | biodegradation of DEET | g/m3/d |
| r30 | adsorption of DEET | g/m3 |
| r31 | desorption of DEET | g/m3/d |
| r32 | biodegradation of caffeine | g/m3/d |
| r33 | adsorption of caffeine | g/m3 |
| r34 | desorption of caffeine | g/m3/d |
| r35 | biodegradation of theobromine | g/m3/d |
| r36 | adsorption of theobromine | g/m3 |
| r37 | desorption of theobromine | g/m3/d |
| r38 | biodegradation of sucralose | g/m3/d |
| r39 | adsorption of sucralose | g/m3 |
| r40 | desorption of sucralose | g/m3/d |
| r41 | biodegradation of acesulfame-K | g/m3/d |
| r42 | adsorption of acesulfame-K | g/m3 |
| r43 | desorption of acesulfame-K | g/m3/d |
| r44 | biodegradation of iopromide | g/m3/d |
| r45 | adsorption of iopromide | g/m3 |
| r46 | desorption of iopromide | g/m3/d |
| r47 | biodegradation of iohexol | g/m3/d |
| r48 | adsorption of iohexol | g/m3 |
| r49 | desorption of iohexol | g/m3/d |

|  | xii | si | ss | xi | xs | xbh | xba | xu |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| r1 |  |  | - 1/yh |  |  | 1 |  |  |
| r2 |  |  | - 1/yh |  |  | 1 |  |  |
| r3 |  |  | - 1/yh |  |  | 1 |  |  |
| r4 |  |  | - 1/yh |  |  | 1 |  |  |
| r5 |  |  |  |  | 1-fuh | -1 |  | fuh |
| r6 |  |  | 1 |  | -1 |  |  |  |
| r7 |  |  |  |  |  |  |  |  |
| r8 |  |  |  |  |  |  |  |  |
| r9 |  |  |  |  |  |  | 1 |  |
| r10 |  |  |  |  | 1-fua |  | -1 | fua |
| r11 |  |  |  |  |  | 1 |  |  |
| r12 |  |  |  |  |  |  |  |  |
| r13 |  |  |  |  |  |  |  |  |
| r14 |  |  |  |  |  | 1 |  |  |
| r15 |  |  |  |  |  |  |  |  |
| r16 |  |  |  |  |  |  |  |  |
| r17 |  |  |  |  |  | 1 |  |  |
| r18 |  |  |  |  |  |  |  |  |
| r19 |  |  |  |  |  |  |  |  |
| r20 |  |  |  |  |  | 1 |  |  |
| r21 |  |  |  |  |  |  |  |  |
| r22 |  |  |  |  |  |  |  |  |
| r23 |  |  |  |  |  | 1 |  |  |
| r24 |  |  |  |  |  |  |  |  |
| r25 |  |  |  |  |  |  |  |  |
| r26 |  |  |  |  |  | 1 |  |  |
| r27 |  |  |  |  |  |  |  |  |
| r28 |  |  |  |  |  |  |  |  |
| r29 |  |  |  |  |  | 1 |  |  |
| r30 |  |  |  |  |  |  |  |  |
| r31 |  |  |  |  |  |  |  |  |
| r32 |  |  |  |  |  | 1 |  |  |
| r33 |  |  |  |  |  |  |  |  |
| r34 |  |  |  |  |  |  |  |  |
| r35 |  |  |  |  |  | 1 |  |  |
| r36 |  |  |  |  |  |  |  |  |
| r37 |  |  |  |  |  |  |  |  |
| r38 |  |  |  |  |  | 1 |  |  |
| r39 |  |  |  |  |  |  |  |  |
| r40 |  |  |  |  |  |  |  |  |
| r41 |  |  |  |  |  | 1 |  |  |
| r42 |  |  |  |  |  |  |  |  |
| r43 |  |  |  |  |  |  |  |  |
| r44 |  |  |  |  |  | 1 |  |  |
| r45 |  |  |  |  |  |  |  |  |
| r46 |  |  |  |  |  |  |  |  |
| r47 |  |  |  |  |  | 1 |  |  |
| r48 |  |  |  |  |  |  |  |  |
| r49 |  |  |  |  |  |  |  |  |

|  | so | snh | snd | xnd | sno | snn |
| --- | --- | --- | --- | --- | --- | --- |
| r1 | -(1-yh)/yh | -ibhn |  |  |  |  |
| r2 |  | -ibhn |  |  | -(1-yh)/(2.86*yh) | (1 - yh)/(2.86*yh) |
| r3 | -(1-yh)/yh |  |  |  | -ibhn |  |
| r4 |  |  |  |  | -ibhn -(1-yh)/(2.86*yh) | (1 - yh)/(2.86*yh) |
| r5 |  |  |  | ibhn - fuh*iuhn |  |  |
| r6 |  |  |  |  |  |  |
| r7 |  |  | 1 | -1 |  |  |
| r8 |  | 1 | -1 |  |  |  |
| r9 | -(4.57-ya)/ya | -ibhn-1/ya |  |  | 1/ya |  |
| r10 |  |  |  | ibhn - fua*iuhn |  |  |
| r11 |  |  |  |  |  |  |
| r12 |  |  |  |  |  |  |
| r13 |  |  |  |  |  |  |
| r14 |  |  |  |  |  |  |
| r15 |  |  |  |  |  |  |
| r16 |  |  |  |  |  |  |
| r17 |  |  |  |  |  |  |
| r18 |  |  |  |  |  |  |
| r19 |  |  |  |  |  |  |
| r20 |  |  |  |  |  |  |
| r21 |  |  |  |  |  |  |
| r22 |  |  |  |  |  |  |
| r23 |  |  |  |  |  |  |
| r24 |  |  |  |  |  |  |
| r25 |  |  |  |  |  |  |
| r26 |  |  |  |  |  |  |
| r27 |  |  |  |  |  |  |
| r28 |  |  |  |  |  |  |
| r29 |  |  |  |  |  |  |
| r30 |  |  |  |  |  |  |
| r31 |  |  |  |  |  |  |
| r32 |  |  |  |  |  |  |
| r33 |  |  |  |  |  |  |
| r34 |  |  |  |  |  |  |
| r35 |  |  |  |  |  |  |
| r36 |  |  |  |  |  |  |
| r37 |  |  |  |  |  |  |
| r38 |  |  |  |  |  |  |
| r39 |  |  |  |  |  |  |
| r40 |  |  |  |  |  |  |
| r41 |  |  |  |  |  |  |
| r42 |  |  |  |  |  |  |
| r43 |  |  |  |  |  |  |
| r44 |  |  |  |  |  |  |
| r45 |  |  |  |  |  |  |
| r46 |  |  |  |  |  |  |
| r47 |  |  |  |  |  |  |
| r48 |  |  |  |  |  |  |
| r49 |  |  |  |  |  |  |

|  | salk | sza | xza | szb | xzb | szc | xzc | szd | xzd |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| r1 | - ibhn/14. |  |  |  |  |  |  |  |  |
| r2 | (- ibhn/14.) + ((1 - yh)/(14*2.86*yh)) |  |  |  |  |  |  |  |  |
| r3 | - ibhn/14. |  |  |  |  |  |  |  |  |
| r4 | (- ibhn/14.) + ((1 - yh)/(14*2.86*yh)) |  |  |  |  |  |  |  |  |
| r5 |  |  |  |  |  |  |  |  |  |
| r6 |  |  |  |  |  |  |  |  |  |
| r7 |  |  |  |  |  |  |  |  |  |
| r8 | 1/14. |  |  |  |  |  |  |  |  |
| r9 | (- ibhn/14.) - 1./(ya*7) |  |  |  |  |  |  |  |  |
| r10 |  |  |  |  |  |  |  |  |  |
| r11 |  | -1 |  |  |  |  |  |  |  |
| r12 |  | -1 | 1 |  |  |  |  |  |  |
| r13 |  | 1 | -1 |  |  |  |  |  |  |
| r14 |  |  |  | -1 |  |  |  |  |  |
| r15 |  |  |  | -1 | 1 |  |  |  |  |
| r16 |  |  |  | 1 | -1 |  |  |  |  |
| r17 |  |  |  |  |  | -1 |  |  |  |
| r18 |  |  |  |  |  | -1 | 1 |  |  |
| r19 |  |  |  |  |  | 1 | -1 |  |  |
| r20 |  |  |  |  |  |  |  | -1 |  |
| r21 |  |  |  |  |  |  |  | -1 | 1 |
| r22 |  |  |  |  |  |  |  | 1 | -1 |
| r23 |  |  |  |  |  |  |  |  |  |
| r24 |  |  |  |  |  |  |  |  |  |
| r25 |  |  |  |  |  |  |  |  |  |
| r26 |  |  |  |  |  |  |  |  |  |
| r27 |  |  |  |  |  |  |  |  |  |
| r28 |  |  |  |  |  |  |  |  |  |
| r29 |  |  |  |  |  |  |  |  |  |
| r30 |  |  |  |  |  |  |  |  |  |
| r31 |  |  |  |  |  |  |  |  |  |
| r32 |  |  |  |  |  |  |  |  |  |
| r33 |  |  |  |  |  |  |  |  |  |
| r34 |  |  |  |  |  |  |  |  |  |
| r35 |  |  |  |  |  |  |  |  |  |
| r36 |  |  |  |  |  |  |  |  |  |
| r37 |  |  |  |  |  |  |  |  |  |
| r38 |  |  |  |  |  |  |  |  |  |
| r39 |  |  |  |  |  |  |  |  |  |
| r40 |  |  |  |  |  |  |  |  |  |
| r41 |  |  |  |  |  |  |  |  |  |
| r42 |  |  |  |  |  |  |  |  |  |
| r43 |  |  |  |  |  |  |  |  |  |
| r44 |  |  |  |  |  |  |  |  |  |
| r45 |  |  |  |  |  |  |  |  |  |
| r46 |  |  |  |  |  |  |  |  |  |
| r47 |  |  |  |  |  |  |  |  |  |
| r48 |  |  |  |  |  |  |  |  |  |
| r49 |  |  |  |  |  |  |  |  |  |

|  | sze | xze | szf | xzf | szg | xzg | szh | xzh | szi | xzi |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| r1 |  |  |  |  |  |  |  |  |  |  |
| r2 |  |  |  |  |  |  |  |  |  |  |
| r3 |  |  |  |  |  |  |  |  |  |  |
| r4 |  |  |  |  |  |  |  |  |  |  |
| r5 |  |  |  |  |  |  |  |  |  |  |
| r6 |  |  |  |  |  |  |  |  |  |  |
| r7 |  |  |  |  |  |  |  |  |  |  |
| r8 |  |  |  |  |  |  |  |  |  |  |
| r9 |  |  |  |  |  |  |  |  |  |  |
| r10 |  |  |  |  |  |  |  |  |  |  |
| r11 |  |  |  |  |  |  |  |  |  |  |
| r12 |  |  |  |  |  |  |  |  |  |  |
| r13 |  |  |  |  |  |  |  |  |  |  |
| r14 |  |  |  |  |  |  |  |  |  |  |
| r15 |  |  |  |  |  |  |  |  |  |  |
| r16 |  |  |  |  |  |  |  |  |  |  |
| r17 |  |  |  |  |  |  |  |  |  |  |
| r18 |  |  |  |  |  |  |  |  |  |  |
| r19 |  |  |  |  |  |  |  |  |  |  |
| r20 |  |  |  |  |  |  |  |  |  |  |
| r21 |  |  |  |  |  |  |  |  |  |  |
| r22 |  |  |  |  |  |  |  |  |  |  |
| r23 | -1 |  |  |  |  |  |  |  |  |  |
| r24 | -1 | 1 |  |  |  |  |  |  |  |  |
| r25 | 1 | -1 |  |  |  |  |  |  |  |  |
| r26 |  |  | -1 |  |  |  |  |  |  |  |
| r27 |  |  | -1 | 1 |  |  |  |  |  |  |
| r28 |  |  | 1 | -1 |  |  |  |  |  |  |
| r29 |  |  |  |  | -1 |  |  |  |  |  |
| r30 |  |  |  |  | -1 | 1 |  |  |  |  |
| r31 |  |  |  |  | 1 | -1 |  |  |  |  |
| r32 |  |  |  |  |  |  | -1 |  |  |  |
| r33 |  |  |  |  |  |  | -1 | 1 |  |  |
| r34 |  |  |  |  |  |  | 1 | -1 |  |  |
| r35 |  |  |  |  |  |  |  |  | -1 |  |
| r36 |  |  |  |  |  |  |  |  | -1 | 1 |
| r37 |  |  |  |  |  |  |  |  | 1 | -1 |
| r38 |  |  |  |  |  |  |  |  |  |  |
| r39 |  |  |  |  |  |  |  |  |  |  |
| r40 |  |  |  |  |  |  |  |  |  |  |
| r41 |  |  |  |  |  |  |  |  |  |  |
| r42 |  |  |  |  |  |  |  |  |  |  |
| r43 |  |  |  |  |  |  |  |  |  |  |
| r44 |  |  |  |  |  |  |  |  |  |  |
| r45 |  |  |  |  |  |  |  |  |  |  |
| r46 |  |  |  |  |  |  |  |  |  |  |
| r47 |  |  |  |  |  |  |  |  |  |  |
| r48 |  |  |  |  |  |  |  |  |  |  |
| r49 |  |  |  |  |  |  |  |  |  |  |

|  | szj | xzj | szk | xzk | szl | xzl | szm | xzm |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| r1 |  |  |  |  |  |  |  |  |
| r2 |  |  |  |  |  |  |  |  |
| r3 |  |  |  |  |  |  |  |  |
| r4 |  |  |  |  |  |  |  |  |
| r5 |  |  |  |  |  |  |  |  |
| r6 |  |  |  |  |  |  |  |  |
| r7 |  |  |  |  |  |  |  |  |
| r8 |  |  |  |  |  |  |  |  |
| r9 |  |  |  |  |  |  |  |  |
| r10 |  |  |  |  |  |  |  |  |
| r11 |  |  |  |  |  |  |  |  |
| r12 |  |  |  |  |  |  |  |  |
| r13 |  |  |  |  |  |  |  |  |
| r14 |  |  |  |  |  |  |  |  |
| r15 |  |  |  |  |  |  |  |  |
| r16 |  |  |  |  |  |  |  |  |
| r17 |  |  |  |  |  |  |  |  |
| r18 |  |  |  |  |  |  |  |  |
| r19 |  |  |  |  |  |  |  |  |
| r20 |  |  |  |  |  |  |  |  |
| r21 |  |  |  |  |  |  |  |  |
| r22 |  |  |  |  |  |  |  |  |
| r23 |  |  |  |  |  |  |  |  |
| r24 |  |  |  |  |  |  |  |  |
| r25 |  |  |  |  |  |  |  |  |
| r26 |  |  |  |  |  |  |  |  |
| r27 |  |  |  |  |  |  |  |  |
| r28 |  |  |  |  |  |  |  |  |
| r29 |  |  |  |  |  |  |  |  |
| r30 |  |  |  |  |  |  |  |  |
| r31 |  |  |  |  |  |  |  |  |
| r32 |  |  |  |  |  |  |  |  |
| r33 |  |  |  |  |  |  |  |  |
| r34 |  |  |  |  |  |  |  |  |
| r35 |  |  |  |  |  |  |  |  |
| r36 |  |  |  |  |  |  |  |  |
| r37 |  |  |  |  |  |  |  |  |
| r38 | -1 |  |  |  |  |  |  |  |
| r39 | -1 | 1 |  |  |  |  |  |  |
| r40 | 1 | -1 |  |  |  |  |  |  |
| r41 |  |  | -1 |  |  |  |  |  |
| r42 |  |  | -1 | 1 |  |  |  |  |
| r43 |  |  | 1 | -1 |  |  |  |  |
| r44 |  |  |  |  | -1 |  |  |  |
| r45 |  |  |  |  | -1 | 1 |  |  |
| r46 |  |  |  |  | 1 | -1 |  |  |
| r47 |  |  |  |  |  |  | -1 |  |
| r48 |  |  |  |  |  |  | -1 | 1 |
| r49 |  |  |  |  |  |  | 1 | -1 |

# Appendix D: Kinetic Equations

|  | Description | Kinetic Equation |
| --- | --- | --- |
| r1 | aerobic growth of heterotrophs on soluble substrate with ammonia as N source | muh*MssHET*MsoHET*MsnhGEN*salksatHET*xbh |
| r2 | anoxic growth of heterotrophs on soluble substrate with ammonia as N source | etag*muh*MssHET*inhibsoaxHET*MsnoHET*MsnhGEN*salksatHET*xbh |
| r3 | aerobic growth of heterotrophs on soluble substrate with nitrate as N source | muh*MssHET*MsoHET*inhibsnhHET*MsnoHET*salksatHET*xbh |
| r4 | anoxic growth of heterotrophs soluble substrate with nitrate as N source | etag*muh*MssHET*inhibsoaxHET*inhibsnhHET*MsnoHET*salksatHET*xbh |
| r5 | decay of heterotrophs | bh*xbh |
| r6 | hydrolysis of entrapped organics | kh* (subsatHET)*(MsoHET + etah*inhibsoo2HET*MsnoHET)*xbh |
| r7 | hydrolysis of entrapped organic nitrogen | r6*(xnd/(xs)) |
| r8 | ammonification of soluble organic nitrogen | ka*snd*xbh |
| r9 | growth of autotrophs | mua*MsnhGEN*MsnhNIT*MsoNIT*salksatAUT*xba |
| r10 | decay of autotrophs | ba*xba |
| r11 | biodegradation of E1 | kbioE1*sza*xbh |
| r12 | adsorption of E1 | kdE1*sza*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r13 | desorption of E1 | kdes*xza |
| r14 | biodegradation of atenolol | kbioate*szb*xbh |
| r15 | adsorption of atenolol | kdate*szb*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r16 | desorption of atenolol | kdes*xzb |
| r17 | biodegradation of lopressor | kbiolop*szc*xbh |
| r18 | adsorption of lopressor | kdlop*szc*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r19 | desorption of lopressor | kdes*xzc |
| r20 | biodegradation of meprobamate | kbiomep*szd*xbh |
| r21 | adsorption of meprobamate | kdmep*szd*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r22 | desorption of meprobamate | kdes*xzd |
| r23 | biodegradation of triclosan | kbiotri*sze*xbh |
| r24 | adsorption of triclosan | kdtri*sze*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r25 | desorption of triclosan | kdes*xze |
| r26 | biodegradation of gemfibrozil | kbiogem*szf*xbh |
| r27 | adsorption of gemfibrozil | kdgem*szf*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r28 | desorption of gemfibrozil | kdes*xzf |
| r29 | biodegradation of DEET | kbioDEET*szg*xbh |
| r30 | adsorption of DEET | kdDEET*szg*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r31 | desorption of DEET | kdes*xzg |
| r32 | biodegradation of caffeine | kbiocaf*szh*xbh |
| r33 | adsorption of caffeine | kdcaf*szh*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r34 | desorption of caffeine | kdes*xzh |
|  | Description | Kinetic Equation |
| r35 | biodegradation of theobromine | kbiothe*szi*xbh |
| r36 | adsorption of theobromine | kdthe*szi*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r37 | desorption of theobromine | kdes*xzi |
| r38 | biodegradation of sucralose | kbiosuc*szj*xbh |
| r39 | adsorption of sucralose | kdsuc*szj*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r40 | desorption of sucralose | kdes*xzj |
| r41 | biodegradation of acesulfame-K | kbioace*szk*xbh |
| r42 | adsorption of acesulfame-K | kdace*szk*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r43 | desorption of acesulfame-K | kdes*xzk |
| r44 | biodegradation of iopromide | kbioiop*szl*xbh |
| r45 | adsorption of iopromide | kdiop*szl*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r46 | desorption of iopromide | kdes*xzl |
| r47 | biodegradation of iohexol | kbioioh*szm*xbh |
| r48 | adsorption of iohexol | kdioh*szm*(xs+xbh+xba+xsto+xbp+xbt+xgly+xi+xu)/icv |
| r49 | desorption of iohexol | kdes*xzm |

# Appendix E: Kinetic Parameters

| Cryptic Name | Variable Name | Value at 10ºC | Value at 20ºC | Arrhenius Coefficient | Units |
| --- | --- | --- | --- | --- | --- |
| Active Heterotrophic Biomass |  |  |  |  |  |
| muh | heterotrophic maximum specific growth rate |  | 3.2 | 1.072 | 1/d |
| ksh | readily biodegradable substrate half saturation coefficient |  | 5 |  | gCOD/m3 |
| koh | aerobic oxygen half saturation coefficient |  | 0.2 |  | gO2/m3 |
| kad | anoxic oxygen half saturation coefficient |  | 0.2 |  | gO2/m3 |
| etag | anoxic growth factor |  | 0.5 |  | - |
| kno | nitrate half saturation coefficient |  | 0.1 |  | gN/m3 |
| knh | ammonia (as nutrient) half saturation coefficient |  | 0.05 |  | gN/m3 |
| bh | heterotrophic decay rate |  | 0.62 | 1.029 | 1/d |
| kalk | alkalinity half saturation coefficient |  | 0.1 |  | mole/m3 |
| Active Autotrophic Biomass |  |  |  |  |  |
| mua | autotrophic maximum specific growth rate |  | 0.9 | 1.072 | 1/d |
| kna | ammonia (as substrate) half saturation coefficient |  | 0.7 |  | gN/m3 |
| koa | oxygen half saturation coefficient |  | 0.25 |  | gO2/m3 |
| ba | autotrophic decay rate |  | 0.17 | 1.029 | 1/d |
| kalka | alkalinity half saturation coefficient for autotrophic growth |  | 0.5 |  | mole/m3 |
| Hydrolysis |  |  |  |  |  |
| kh | maximum specific hydrolysis rate |  | 3 | 1.072 | 1/d |
| kx | slowly biodegradable substrate half saturation coefficient |  | 0.1 |  | gCOD/gCOD |
| etah | anoxic hydrolysis factor |  | 0.6 |  | - |
| Ammonification |  |  |  |  |  |
| ka | ammonification rate |  | 0.08 | 1.072 | m3/gCOD/d |
| High Concentration Inhibition |  |  |  |  |  |
| kxbh | high concentration inhibition for heterotrophs |  | 30000 |  | gCOD/m3 |
| kxba | high concentration inhibition for autotrophs |  | 5000 |  | gCOD/m3 |

| Cryptic Name | Variable Name | Value at 10ºC | Value at 20ºC | Arrhenius Coefficient | Units |
| --- | --- | --- | --- | --- | --- |
| Biodegradation Constants |  |  |  |  |  |
| kbioE1 | biodegradation of E1 |  | 0.162 | 1.072 | m3/g/d |
| kbioate | biodegradation of atenolol |  | 0.0042 | 1.072 | m3/g/d |
| kbiolop | biodegradation of lopressor |  |  | 1.072 | m3/g/d |
| kbiomep | biodegradation of meprobamate |  | 0 | 1.072 | m3/g/d |
| kbiotri | biodegradation of triclosan |  | 0.0012 | 1.072 | m3/g/d |
| kbiogem | biodegradation of gemfibrozil |  | 0 | 1.072 | m3/g/d |
| kbioDEET | biodegradation of DEET |  | 0.0015 | 1.072 | m3/g/d |
| kbiocaf | biodegradation of caffeine |  | 0.04 | 1.072 | m3/g/d |
| kbiothe | biodegradation of theobromine |  | 0.038 | 1.072 | m3/g/d |
| kbiosuc | biodegradation of sucralose |  | 0.0000065 | 1.072 | m3/g/d |
| kbioace | biodegradation of acesulfame-K |  | 0.01 | 1.072 | m3/g/d |
| kbioiop | biodegradation of iopromide |  | 0.0075 | 1.072 | m3/g/d |
| kbioioh | biodegradation of iohexol |  | 0.0008 | 1.072 | m3/g/d |
| Adsorption Constants |  |  |  |  |  |
| kdE1 | adsorption of E1 |  | 0.00017 | 1.072 | m3/g |
| kdate | adsorption of atenolol |  | 0.0003 | 1.072 | m3/g |
| kdlop | adsorption of lopressor |  |  | 1.072 | m3/g |
| kdmep | adsorption of meprobamate |  | 0.00079 | 1.072 | m3/g |
| kdtri | adsorption of triclosan |  | 0.001905 | 1.072 | m3/g |
| kdgem | adsorption of gemfribrozil |  | 0.0004 | 1.072 | m3/g |
| kdDEET | adsorption of DEET |  | 0.0001 | 1.072 | m3/g |
| kdcaf | adsorption of caffeine |  | 0.0002 | 1.072 | m3/g |
| kdthe | adsorption of theobromine |  | 0.0002 | 1.072 | m3/g |
| kdsuc | adsorption of sucralose |  | 0.00054 | 1.072 | m3/g |
| kdace | adsorption of acesulfame-K |  | 0.00017 | 1.072 | m3/g |
| kdiop | adsorption of iopromide |  | 0.000036 | 1.072 | m3/g |
| kdioh | adsorption of iohexol |  | 0 | 1.072 | m3/g |
| kdes | desorption coefficient |  | 0.1 | 1.072 | 1/d |